**Price Architectural Perforated Face Supply Diffuser**

**Division 23 – Heating, Ventilating, and Air Conditioning**

**Section 23 37 13 – Diffusers, Registers, and Grilles**

The following specification is for a defined application. Price would be pleased to assist in developing a specification for your specific need.

**PART 1 – GENERAL**

* 1. **Section includes**:
1. Perforated Supply
	1. **Related Requirements**
2. Section 01 30 00 – Administrative Requirements
3. Section 01 40 00 – Quality Requirements
4. Section 01 74 21 – Construction/Demolition Waste Management and Disposal
5. Section 01 78 00 – Closeout Submittals
6. Section 01 79 00 – Demonstration and Training
	1. **Reference Standards**
7. All referenced standards and recommended practices in this section pertain to the most recent publication thereof, including all addenda and errata.
8. ASHRAE 55 – Standard for Thermal Environmental Conditions for Human Occupancy
9. ASHRAE 70 – Standard Method of Testing the Performance of Air Outlets and Air Inlets
10. ASTM D610 – Standard Practice for Evaluating Degree of Rusting on Painted Steel Surfaces
11. ASTM D714 – Test Method for Evaluating Degree of Blistering of Paints
12. ASTM D1308 – Standard Test Method for Effect of Household Chemicals on Clear and Pigmented Organic Finishes
13. ASTM D1654 – Standard Test Method for Evaluation of Painted or Coated Specimens Subjected to Corrosive Environments
14. ASTM D4752 – Standard Practice for Measuring MEK Resistance of Ethyl Silicate (Inorganic) Zinc-Rich Primers by Solvent Rub
15. NFPA 90A – Standard for the Installation of Air-Conditioning and Ventilating Systems

**1.04 Submittals**

1. See Section 01 30 00 – Administrative Requirements for submittal procedures.
2. Product Data: Provide data indicating configuration, general assembly, and materials used in fabrication. Include catalog performance ratings that indicate airflow, and NC designation.
3. Shop Drawings: Indicate configuration, general assembly, and materials used in fabrication.
4. Project Record Documents: Record actual locations of units and control components.
5. Operation and Maintenance Data: Include manufacturer's descriptive literature, operating instructions (if applicable), and maintenance and repair data.
6. Warranty: Submit manufacturer warranty and ensure forms have been completed in Owner's name and registered with manufacturer.
7. Maintenance Materials: Furnish the following for Owner's use in maintenance of project.

**1.06 Quality Assurance**

1. Manufacturer Qualifications: Company specializing in manufacturing the type of products specified in this section, with minimum ten years of documented experience.

**1.07 Warranty**

1. See Section 01 78 00 - Closeout Submittals, for additional warranty requirements.
2. Provide 12 month manufacturer warranty from date of shipment of diffusers.

**PART 2 – PRODUCTS**

**2.01 Manufacturer**

1. Basis of Design: Price Industries, Inc.
2. Architectural Perforated Face Supply Diffuser: Model PDS
3. General:
	1. The perforated face supply diffuser shall provide ducted supply airflow, and shall be supplied to match return air models in appearance and detail.

**2.02 Perforated Ceiling Supply Diffuser**

1. Description:
	1. Furnish and install Price model PDS supply diffusers in sizes and capacities as shown by the plans and air distribution schedule.
2. Construction:
	1. The diffuser shall include fully adjustable louvered pattern controllers mounted on the face panel. The pattern controllers shall permit four-way, three-way, two-way, two-way corner, or one-way airflow patterns.
	2. The diffuser shall have a [square] or [round] neck as indicated on the drawing or diffuser schedule.
	3. The backpan and perforated face shall be coated steel construction, with snap-in mounting to the extruded aluminum border and mounting frame. The framed face panel sub-assembly shall connect to the backpan with spring clip latches for ease of removal and access to pattern controllers.
	4. When installed, the face panel shall be flush with the border frame.
3. Performance:
	1. Air deflector modules shall allow full field adjustment of airflow pattern from one-way to four-way discharge without affecting the free area or the pressure and noise performance of the diffuser.
4. Paint Specification:
	1. Paint finish shall be (**select one**):
		1. Baked-on powder coat finish.
			1. The paint film thickness shall be a minimum of 2 mils.
			2. The finish shall have a hardness of 2H as tested in accordance with ASTM D3363.
			3. The finish shall pass an ASTM B117 Corrosive Environment Salt Spray Test for 1000 hours with no measurable creep, rusting or blistering as per ASTM D1654, D610 and D714.
			4. The finish shall pass an ASTM D870 Water Immersion test of a minimum of 500 hours with no measurable with no rusting or blistering as per ASTM D610 and D714.
			5. The finish shall have an impact resistance of 100 inch-pounds in accordance with ASTM D2794.
		2. All components shall have a custom finish in a color to match a customer supplied sample.
5. Mounting Frame:
	1. The diffuser mounting frame shall be suitable for lay-in or surface mount applications with the following frame style (**select one**):
		1. Surface mount
6. Magnetic Resonance Imaging (MRI) Construction:
	1. The diffuser shall be supplied with an all-aluminum construction for MRI applications.
	2. The MRI option does not include a volume control damper.

**PART 3 – EXECUTION**

**3.01 Examination**

1. Verify that conditions are suitable for installation.
2. Verify that field measurements are as shown on the drawings.

**3.02 Installation**

1. Install in accordance with manufacturer’s instructions.
2. See drawings for the size(s) and locations of diffusers.

**3.03 Field Quality Control**

1. See Section 01 40 00 – Quality Requirements for additional requirements.

**3.05 Cleaning**

1. See Section 01 74 19 – Construction Waste Management and Disposal for additional requirements.

**3.06 Closeout Activities**

1. See Section 01 78 00 – Closeout Submittals for closeout documentation requirements.
2. See Section 01 79 00 – Demonstration and Training for additional requirements.