## CF_CFP
Input | [10 empty] | Output
The template below indicates all the viable architectural linear slot diffuser (CF - Custom Flow) selections that have performance available through the Price Toolkit. Select desired configurations from the drop down cell options below. Red text indicates the input value is outside the allowable range for performance. See performance notes for details. Dark grey cells will be automatically populated. Hide unrequired columns. DO NOT DELETE COLUMNS. To create new rows, copy and paste previous row. Note: The input menu options reference values in the Lookup Tables tab. DO NOT DELETE LOOKUP TABLES TAB. | [10 empty] | Performance for the selected options are shown below. If the configured options are valid (See Limitation guide) and performance is still not available, refer to the online calaogue performance for acceptable ranges of cfm.
(https://www.priceindustries.com/content/uploads/assets/literature/catalogs/catalog-pages/section%20a/cf-custom-flow-architectural-slot-diffuser-catalog.pdf)
Model | Projection | Pattern Controller | No. of Slots | Slot Width [in] | Inlet Size [in] |  | Length [in] | AirFlow [cfm] | ∆T [F] | Pattern | Velocity [fpm] | Throw150 [ft] | Throw100 [ft] | Throw50 [ft] | Noise Criteria [NC] | Total Pressure [in. w.g.] | Velocity Pressure [in. w.g.] | Static Pressure [in. w.g.] | Warning Notes
CF - Custom Flow | Horizontal | AS | 1 | 3 |  |  | 31.452 | 125 | 60 |  | 272.9043 | 7 | 13 | 27 | -- | 0.015 | 0.005 | 0.01
CF - Custom Flow | Vertical | JS | 2 | 1.5 |  |  | 100 | 400 | 0 |  | No performance data was found. | No performance data was found. | No performance data was found. | No performance data was found. | No performance data was found. | No performance data was found. | No performance data was found. | No performance data was found. | Select CFM value between 500 and 1750
CFP - Custom Flow Plenum | Horizontal | AS | 1 | 2 | 8 | 8" Round | 24 | 200 | 0 |  | 573.0659 | 20 | 26 | 37 | 33 | 0.263 | 0.02 | 0.242
CFP - Custom Flow Plenum | Vertical | JS | 1 | 3 | 6 | 6" Round | 24 | 150 | 0 |  | 765.3061 | 3 | 6 | 15 | -- | 0.056 | 0.037 | 0.02
CFT - Custom Flow Integrated T-Bar Module | Horizontal | AS | 1 | 3 | 10 | 10" Round | 48 | 300 | 0 |  | 550.4587 | 10 | 15 | 25 | 18 | 0.07 | 0.019 | 0.052
CFT - Custom Flow Integrated T-Bar Module | Vertical | AS | 2 | 3 | 12 | 12" Round | 60 | 400 | 0 |  | No performance data was found. | No performance data was found. | No performance data was found. | No performance data was found. | No performance data was found. | No performance data was found. | No performance data was found. | No performance data was found.
CF Performance Limits
Linear Length = 24" - 120"
Plenum Length = 24" - 60"
Slot Width = 1" - 3"
Slot Quantity = 1 - 2
*Available Round Inlet Size = 6", 8", 10", 12"
*Available Oval Inlet Size = 8" x 10.945" (12" Round Equivalent), 8 x 14.087" (14" Round Equivalent)
*Available inlet size will vary depending on slot quantity and slot width
CF Performance Notes
1. JS pattern controller performance is for vertical throw.
2. AS pattern controller performance is for horizontal performance.
3. CF performance is without plenum.
4. "--" indicates NC is less than 15.
5. Negative Temp Differential indicates cooling. -20 max
6. Positive temp differenctial indicates heating +40 max
7. For return performance please reach out to the applications team grd@priceindustries.com
LEGEND
Empty Cell
Cell Automatically Populated
Input Value/Select from Drop Down
Incorrect Value/
Outside of Allowable Range for Performance
TEXT

## SDS_SDR
Input | [9 empty] | Output
The template below indicates all the viable Linear Slot Diffuser (SDS) selections that have performance available through the Price Toolkit. Select desired configurations from the drop down cell options below. Red text indicates the input value is outside the allowable range for performance. See performance notes for details. Dark grey cells will be automatically populated. Hide unrequired columns. DO NOT DELETE COLUMNS. To create new rows, copy and paste previous row. Note: The input menu options reference values in the Lookup Tables tab. DO NOT DELETE LOOKUP TABLES TAB. | [9 empty] | Performance for the selected options are shown below. If the configured options are valid (See Limitation guide) and performance is still not available, refer to the online calaogue performance for acceptable ranges of cfm.
(https://www.priceindustries.com/content/uploads/assets/literature/catalogs/catalog-pages/section%20a/sds-linear-slot-diffuser-catalog.pdf)
Model | Projection | Pattern Controller | No. of Slots | Slot Width | Inlet Size | Length [in] | AirFlow [cfm] | ∆T [F] | Pattern | Velocity [fpm] | Throw150 [ft] | Throw100 [ft] | Throw50 [ft] | Noise Criteria [NC] | Total Pressure [in. w.g.] | Velocity Pressure [in. w.g.] | Static Pressure [in. w.g.] | Warning Notes
SDS50 - Linear Slot Supply 1/2 Slot | Vertical |  | 1 |  |  | 24 | 75 | 0 |  | 937.5 |  |  | 12 | -- | 0.178 | 0.055 | 0.123
SDS75 - Linear Slot Supply 3/4 Slot | Vertical |  | 2 |  |  | 36 | 200 | 0 |  | 656.168 |  |  | 20 | -- | 0.081 | 0.027 | 0.054
SDS100 - Linear Slot Supply 1 Slot | Vertical |  | 3 |  |  | 48 | 400 | 0 |  | 526.5929 |  |  | 27 | -- | 0.041 | 0.017 | 0.024
SDS50 - Linear Slot Supply 1/2 Slot | Horizontal |  | 4 |  |  | 60 | 200 | 0 |  | 400 | 4 | 9 | 19 | -- | 0.018 | 0.01 | 0.008
SDS75 - Linear Slot Supply 3/4 Slot | Horizontal |  | 5 |  |  | 72 | 300 | -30 |  | 324.6753 | 3 | 6 | 14 | -- | 0.01 | 0.007 | 0.004
SDS100 - Linear Slot Supply 1 Slot | Horizontal |  | 6 |  |  | 84 | 400 | 0 |  | 253.9683 | 5 | 11 | 22 | -- | 0.006 | 0.004 | 0.002
SDR50 - Linear Slot Return 1/2 Slot | Vertical |  | 7 |  |  | 96 | 600 | 0 |  | 267.8571 |  |  |  | -- | 0.017 | 0.004 | 0.013
SDR75 - Linear Slot Return 3/4 Slot | Vertical |  | 8 |  |  | 108 | 500 | 0 |  | No performance data was found. | No performance data was found. | No performance data was found. | No performance data was found. | No performance data was found. | No performance data was found. | No performance data was found. | No performance data was found. | Select CFM value between 720 and 5760
SDR100 - Linear Slot Return 1 Slot | Vertical |  | 1 |  |  | 120 | 500 | 0 |  | 789.8894 |  |  |  | 25 | 0.15 | 0.039 | 0.111
SDS/SDR Performance Limits
Slot Quantity = 1 - 8
Length = 8" - 360"
Slot Width = 0.5" - 1"
SDS/SDR Performance Notes
1. See catalog performance for SDS150 diffusers, and SDB and SDA plenums
2. Please contact a sale representative for SDS/SDR performance with slot quantity greater than 8
3. Performance for SDR diffusers is available for vertical projection only.
4. Throw performance for vertical projection is given at terminal velcoity (T50) only
5. Negative Temp Differential indicates cooling. -20 max
6. Positive temp differenctial indicates heating +40 max
7. "--" indicates NC is less than 15.
LEGEND
Empty Cell
Cell Automatically Populated
Input Value/Select from Dropdown
Incorrect Value/
Outside of Allowable Range for Performance
TEXT

## TBD
Input | [11 empty] | Output
The template below indicates all the viable Tee Bar Diffuser (TBD) selections that have performance available through the Price Toolkit. Select desired configurations from the drop down cell options below. Red text indicates the input value is outside the allowable range for performance. See performance notes for details. Dark grey cells will be automatically populated. Hide unrequired columns. DO NOT DELETE COLUMNS. To create new rows, copy and paste previous row. Note: The input menu options reference values in the Lookup Tables tab. DO NOT DELETE LOOKUP TABLES TAB. | [11 empty] | Performance for the selected options are shown below. If the configured options are valid (See Limitation guide) and performance is still not available, refer to the online calaogue performance for acceptable ranges of cfm.
(https://www.priceindustries.com/content/uploads/assets/literature/catalogs/tbd2348-t-bar-diffuser-catalog.pdf)
Model | Projection | Pattern Controller | No. of Slots | Slot Width [in] | Slot Width [in] | Inlet Size [in] |  | Length [in] | AirFlow [cfm] | ∆T [F] | Pattern | Velocity [fpm] | Throw150 [ft] | Throw100 [ft] | Throw50 [ft] | Noise Criteria [NC] | Total Pressure [in. w.g.] | Velocity Pressure [in. w.g.] | Static Pressure [in. w.g.] | Warning Notes
TBDI6HC - Thermal Powered Auto-Changeover Heat/Cool Diffuser | Horizontal |  |  |  | 1.75 | 6x8.937 | Oval (8" Round Equivalent) | 24 | 100 | 0 |  | 311.2356 | 9 | 13 | 23 | -- | 0.081 | 0.006 | 0.075
TBD2100 - T-Bar Curved Extruded Blade 1 Slot | Horizontal |  | 2 |  | 1 | 4x7 | Oval (6" Round Equivalent) | 24 | 100 | 0 |  | 509.2958 | 6 | 9 | 18 | 18 | 0.071 | 0.016 | 0.054
TBDI2150 - Insulated T-Bar Curved Extruded Blades 1 1/2 Sl | Horizontal |  | 1 |  | 1.5 | 4x13.250 | Oval (10" Round Equivalent) | 24 | 400 | 0 |  | No performance data was found. | No performance data was found. | No performance data was found. | No performance data was found. | No performance data was found. | No performance data was found. | No performance data was found. | No performance data was found. | Review performance submittal for valid CFM.
TBD350 - T-Bar Diffuser Ice-Tong Blades 1/2 Slot | Horizontal |  | 2 |  | 0.5 | 4x10.125 | Oval (8" Round Equivalent) | 24 | 150 | 0 |  | 443.4685 | 15 | 22 | 31 | 35 | 0.209 | 0.012 | 0.196
TBD375 - T-Bar Diffuser Ice-Tong Blades 3/4 Slot | Horizontal |  | 1 |  | 0.75 | 6 | 6" Round | 24 | 200 | 0 |  | 1062.3971 | 21 | 25 | 36 | 68 | 1.055 | 0.07 | 0.985
TBDI4100 - Insul T-Bar Supp Diff Straight Blades 1 Slots | Horizontal |  | 2 |  | 1 | 6x8.937 | Oval (8" Round Equivalent) | 24 | 300 | 0 |  | 886.9369 | 18 | 26 | 36 | 48 | 0.525 | 0.049 | 0.476
TBDI4150 - Insul T-Bar Supp Diff Straight Blade 1 1/2 Slot | Horizontal |  | 3 |  | 1.5 | 4x13.250 | Oval (10" Round Equivalent) | 24 | 400 | 0 |  | 752.0702 | 18 | 27 | 42 | 29 | 0.177 | 0.035 | 0.142
TBD638 - High Induction T-Bar Supply Diffuser 3/8 Slot | Horizontal |  |  |  | 0.375 | 4x7 | Oval (6" Round Equivalent) | 24 | 100 | 0 |  | 531.1985 | 6 | 9 | 18 | 18 | 0.144 | 0.018 | 0.126
TBDI6HC - Thermal Powered Auto-Changeover Heat/Cool Diffuser | Horizontal |  |  |  | 1.75 | 6x12.078 | Oval (10" Round Equivalent) | 24 | 200 | 0 |  | 448.1291 | 18 | 23 | 32 | 29 | 0.213 | 0.013 | 0.2
TBDI6HC - Thermal Powered Auto-Changeover Heat/Cool Diffuser | Vertical |  |  |  | 0.375 | 6x8.937 | Oval (8" Round Equivalent) | 24 | 200 | 10 |  | 622.4712 | 17 | 21 | 30 | 41 | 0.466 | 0.024 | 0.442
TBD7 - T-Bar Supp Diff Vane Fixed Patt Control 3/4Slot | Horizontal |  | 3 |  | 0.75 | 8 | 8" Round | 24 | 400 | 10 | 1W-A | 1146.1318 | 19 | 23 | 33 | 37 | 0.43 | 0.082 | 0.348
TBD475 - T-Bar Straight Blade 3/4 Slot | Horizontal |  | 1 |  | 0.75 | 6x8.937 | Oval (8" Round Equivalent) | 48 | 200 | 10 |  | 591.2913 | 12 | 15 | 22 | 37 | 0.216 | 0.022 | 0.195
TBD Performance Limits
Slot Width = 0.375" - 1.75"
*Available slot widths vary depending on the TBD
Slot Quantity = 1- 4
* Number of slot vary depending on the TBD
*Available Round Inlet Size = 6", 8"
*Available Oval Inlet Size =
4x7 Oval (6" Round Equivalent)
4x10.125 Oval (8" Round Equivalent)
4x13.250 Oval (10" Round Equivalent)
6x8.937 Oval (8" Round Equivalent)
6x12.078 Oval (10" Round Equivalent)
6x15.218 Oval (12" Round Equivalent)
*Available inlet size will vary depending on slot quantity and slot width
Patterns Avaialble =
lW-N 1-Way All Slots Deflecting TOWARD Neck
lW-A 1-Way All Slots Deflecting AWAY FROM Neck
2W-1N 2-Way 1 Slot Deflecting TOWARD Neck
2W-2N 2-Way 2 Slots Deflecting TOWARD Neck
2W-3N 2-Way 3 Slots Deflecting TOWARD Neck
TBD Performance Notes
1. SDS performance is without plenum.
2. Negative Temp Differential indicates cooling. -20 max
3. Positive temp differenctial indicates heating +40 max
4. TBDI6HC Horizontal must be in cooling <-10 F Temp Differential. Vertical Projection Must be in heating >10 F Temp Differential
5. "--" indicates NC is less than 15.
LEGEND
Empty Cell
Cell Automatically Populated
Input Value/Select from Dropdown
Incorrect Value/
Outside of Allowable Range for Performance
TEXT

## Lookup Tables
CF_CFP Lookup Tables
Hide/Unhide the lookup tables as needed. DO NOT DELETE LOOKUP TABLES.
Inlet Sizes Lookup Table
CFT - Custom Flow Integrated T-Bar Module11 | CFT - Custom Flow Integrated T-Bar Module11.5 | CFT - Custom Flow Integrated T-Bar Module12 | CFT - Custom Flow Integrated T-Bar Module12.5 | CFT - Custom Flow Integrated T-Bar Module13 | CFT - Custom Flow Integrated T-Bar Module21 | CFT - Custom Flow Integrated T-Bar Module21.5 | CFT - Custom Flow Integrated T-Bar Module22 | CFT - Custom Flow Integrated T-Bar Module22.5 | CFT - Custom Flow Integrated T-Bar Module23 |  | CFP - Custom Flow Plenum11 | CFP - Custom Flow Plenum11.5 | CFP - Custom Flow Plenum12 | CFP - Custom Flow Plenum12.5 | CFP - Custom Flow Plenum13 | CFP - Custom Flow Plenum21 | CFP - Custom Flow Plenum21.5 | CFP - Custom Flow Plenum22 | CFP - Custom Flow Plenum22.5 | CFP - Custom Flow Plenum23 | CF - Custom Flow11 | CF - Custom Flow11.5 | CF - Custom Flow12 | CF - Custom Flow12.5 | CF - Custom Flow13 | CF - Custom Flow21 | CF - Custom Flow21.5 | CF - Custom Flow22 | CF - Custom Flow22.5 | CF - Custom Flow23
6 | 6 | 8 | 10 | 10 | 8 | 8 | 8 | 10 | 10 |  | 6 | 6 | 8 | 10EQ-8.000x10.945 | 10EQ-8.000x10.945 | 8 | 8 | 8 | 10 | 10
8 | 8 | 10 | 12 | 12 | 10 | 10 | 10 | 12 | 12 |  | 8 | 8 | 10EQ-8.000x10.945 | 12EQ-8.000x14.087 | 12EQ-8.000x14.087 | 10 | 10 | 10 | 12 | 12
10 | 10 | 12 | 10EQ-8.000x10.945 | 10EQ-8.000x10.945 | 12 | 12 | 12 |  |  |  | 10 | 10EQ-8.000x10.945 | 12EQ-8.000x14.087 |  |  | 12 | 12 | 12
12 | 12 | 10EQ-8.000x10.945 | 12EQ-8.000x14.087 | 12EQ-8.000x14.087 | [6 empty] | 12 | 12EQ-8.000x14.087
10EQ-8.000x10.945 | 10EQ-8.000x10.945 | 12EQ-8.000x14.087 | [8 empty] | 10EQ-8.000x10.945
12EQ-8.000x14.087 | 12EQ-8.000x14.087 | [9 empty] | 12EQ-8.000x14.087
| CFM Lookup Table | [5 empty] | Inlet Size Lookup Table
| Slot Qty. | Slot Width | Lookup Code | Minimum cfm/ft | Maximum cfm/ft |  |  |  |  | No Inlet
| 1 | 1 | 11 | 25 | 115 |  | 4x7 | Oval | (6" Round Equivalent)
| 1 | 1.5 | 11.5 | 30 | 120 |  | 4x10.125 | Oval | (8" Round Equivalent)
| 1 | 2 | 12 | 30 | 150 |  | 4x13.250 | Oval | (10" Round Equivalent)
| 1 | 2.5 | 12.5 | 30 | 180 |  | 6x8.937 | Oval | (8" Round Equivalent)
| 1 | 3 | 13 | 30 | 210 |  | 6x12.078 | Oval | (10" Round Equivalent)
| 2 | 1 | 21 | 50 | 200 |  | 6x15.218 | Oval | (12" Round Equivalent)
| 2 | 1.5 | 21.5 | 60 | 210 |  | 10EQ-8.000x10.945 | Oval | (10" Round Equivalent)
| 2 | 2 | 22 | 60 | 270 |  | 12EQ-8.000x14.087 | Oval | (12" Round Equivalent)
| 2 | 2.5 | 22.5 | 60 | 330 |  | 14EQ-8.000x10.945 | Oval | (14" Round Equivalent)
| 2 | 3 | 23 | 60 | 420 |  | 4 | 4" Round
[7 empty] | 6 | 6" Round
[7 empty] | 8 | 8" Round
[7 empty] | 10 | 10" Round
[7 empty] | 12 | 12" Round
SDS_SDR Lookup Tables
Hide/Unhide the lookup tables as needed. DO NOT DELETE LOOKUP TABLES.
Airflow Limits Lookup Table
Lookup Code | Min cfm/ft | Max cfm/ft
SDS50 - Linear Slot Supply 1/2 Slot | 5 | 40
SDS75 - Linear Slot Supply 3/4 Slot | 6 | 48
SDS100 - Linear Slot Supply 1 Slot | 8 | 64
SDR50 - Linear Slot Return 1/2 Slot | 10 | 60
SDR75 - Linear Slot Return 3/4 Slot | 10 | 80
SDR100 - Linear Slot Return 1 Slot | 20 | 100
TBD Lookup Tables
Hide/Unhide the lookup tables as needed. DO NOT DELETE LOOKUP TABLES.
Slot Width Lookup Table |  |  |  | Inlet Size LookupTable
TBD2100 - T-Bar Curved Extruded Blade 1 Slot | Horizontal | 1 |  | 4x7 | Oval | (6" Round Equivalent)
TBD2150 - T-Bar Curved Extruded Blade 1 1/2 Slot | Horizontal | 1.5 |  | 4x10.125 | Oval | (8" Round Equivalent)
TBD3100 - T-Bar Diffuser Ice-Tong Blades 1 Slot | Horizontal | 1 |  | 4x13.250 | Oval | (10" Round Equivalent)
TBD350 - T-Bar Diffuser Ice-Tong Blades 1/2 Slot | Horizontal | 0.5 |  | 6x8.937 | Oval | (8" Round Equivalent)
TBD375 - T-Bar Diffuser Ice-Tong Blades 3/4 Slot | Horizontal | 0.75 |  | 6x12.078 | Oval | (10" Round Equivalent)
TBD4100 - T-Bar Straight Blade 1 Slot | Horizontal | 1 |  | 6x15.218 | Oval | (12" Round Equivalent)
TBD4150 - T-Bar Straight Blade 1 1/2 Slot | Horizontal | 1.5 |  | 4 | 4" Round
TBD475 - T-Bar Straight Blade 3/4 Slot | Horizontal | 0.75 |  | 6 | 6" Round
TBD638 - High Induction T-Bar Supply Diffuser 3/8 Slot | Horizontal | 0.375 |  | 8 | 8" Round
TBD7 - T-Bar Supp Diff Vane Fixed Patt Control 3/4Slot | Horizontal | 0.75
TBDI6HC - Thermal Powered Auto-Changeover Heat/Cool Diffuser | Vertical | 0.375
TBDI6HC - Thermal Powered Auto-Changeover Heat/Cool Diffuser | Horizontal | 1.75
TBDI2100 - Insulated T-Bar Curved Extruded Blades 1 Slot | Horizontal | 1
TBDI2150 - Insulated T-Bar Curved Extruded Blades 1 1/2 Sl | Horizontal | 1.5
TBDI3100 - Insulat T-Bar Supp Diff Ice-Tong Blades 1 Slots | Horizontal | 1
TBDI350 - Insul T-Bar Supp Diff Ice-Tong Blades 1/2 Slots | Horizontal | 0.5
TBDI375 - Insul T-Bar Supply Diff Ice-Tong Blades 3/4Slots | Horizontal | 0.75
TBDI4100 - Insul T-Bar Supp Diff Straight Blades 1 Slots | Horizontal | 1
TBDI4150 - Insul T-Bar Supp Diff Straight Blade 1 1/2 Slot | Horizontal | 1.5
TBDI475 - Insul T-Bar Supp Diff Straight Blades 3/4 Slots | Horizontal | 0.75
TBDI638 - Insul T-Bar Supp Diff High Induction 3/8 Slots | Horizontal | 0.375
TBDI7 - Insul T-Bar Supp Vane Fixed Patt Control 3/4Slot | Horizontal | 0.75
Slot Number Lookup Table
TBD2100 - T-Bar Curved Extruded Blade 1 Slot | TBD2150 - T-Bar Curved Extruded Blade 1 1/2 Slot | TBD3100 - T-Bar Diffuser Ice-Tong Blades 1 Slot | TBD350 - T-Bar Diffuser Ice-Tong Blades 1/2 Slot | TBD375 - T-Bar Diffuser Ice-Tong Blades 3/4 Slot | TBD4100 - T-Bar Straight Blade 1 Slot | TBD4150 - T-Bar Straight Blade 1 1/2 Slot | TBD475 - T-Bar Straight Blade 3/4 Slot | TBD638 - High Induction T-Bar Supply Diffuser 3/8 Slot | TBD7 - T-Bar Supp Diff Vane Fixed Patt Control 3/4Slot | TBDI6HC - Thermal Powered Auto-Changeover Heat/Cool Diffuser | TBDI2100 - Insulated T-Bar Curved Extruded Blades 1 Slot | TBDI2150 - Insulated T-Bar Curved Extruded Blades 1 1/2 Sl | TBDI3100 - Insulat T-Bar Supp Diff Ice-Tong Blades 1 Slots | TBDI350 - Insul T-Bar Supp Diff Ice-Tong Blades 1/2 Slots | TBDI375 - Insul T-Bar Supply Diff Ice-Tong Blades 3/4Slots | TBDI4100 - Insul T-Bar Supp Diff Straight Blades 1 Slots | TBDI4150 - Insul T-Bar Supp Diff Straight Blade 1 1/2 Slot | TBDI475 - Insul T-Bar Supp Diff Straight Blades 3/4 Slots | TBDI638 - Insul T-Bar Supp Diff High Induction 3/8 Slots | TBDI7 - Insul T-Bar Supp Vane Fixed Patt Control 3/4Slot
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1
2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2
|  | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 |  | 3
|  | 4 | 4 | 4 | 4 | 4 | 4 |  | 4 |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 |  | 4
Inlet Size Lookup Table
TBD2100 - T-Bar Curved Extruded Blade 1 Slot | TBD2150 - T-Bar Curved Extruded Blade 1 1/2 Slot | TBD3100 - T-Bar Diffuser Ice-Tong Blades 1 Slot | TBD350 - T-Bar Diffuser Ice-Tong Blades 1/2 Slot | TBD375 - T-Bar Diffuser Ice-Tong Blades 3/4 Slot | TBD4100 - T-Bar Straight Blade 1 Slot | TBD4150 - T-Bar Straight Blade 1 1/2 Slot | TBD475 - T-Bar Straight Blade 3/4 Slot | TBD638 - High Induction T-Bar Supply Diffuser 3/8 Slot | TBD7 - T-Bar Supp Diff Vane Fixed Patt Control 3/4Slot | TBDI6HC - Thermal Powered Auto-Changeover Heat/Cool Diffuser | TBDI2100 - Insulated T-Bar Curved Extruded Blades 1 Slot | TBDI2150 - Insulated T-Bar Curved Extruded Blades 1 1/2 Sl | TBDI3100 - Insulat T-Bar Supp Diff Ice-Tong Blades 1 Slots | TBDI350 - Insul T-Bar Supp Diff Ice-Tong Blades 1/2 Slots | TBDI375 - Insul T-Bar Supply Diff Ice-Tong Blades 3/4Slots | TBDI4100 - Insul T-Bar Supp Diff Straight Blades 1 Slots | TBDI4150 - Insul T-Bar Supp Diff Straight Blade 1 1/2 Slot | TBDI475 - Insul T-Bar Supp Diff Straight Blades 3/4 Slots | TBDI638 - Insul T-Bar Supp Diff High Induction 3/8 Slots | TBDI7 - Insul T-Bar Supp Vane Fixed Patt Control 3/4Slot
4x7 | 4x7 | 4x7 | 4x7 | 4x7 | 4x7 | 4x7 | 4x7 | 4 | 6 | 6x8.937 | 4x7 | 4x7 | 4x7 | 4x7 | 4x7 | 4x7 | 4x7 | 4x7 | 4 | 6
4x10.125 | 4x10.125 | 4x10.125 | 4x10.125 | 4x10.125 | 4x10.125 | 4x10.125 | 4x10.125 | 4x7 | 8 | 6x12.078 | 4x10.125 | 4x10.125 | 4x10.125 | 4x10.125 | 4x10.125 | 4x10.125 | 4x10.125 | 4x10.125 | 4x7 | 8
4x13.250 | 4x13.250 | 4x13.250 | 4x13.250 | 4x13.250 | 4x13.250 | 4x13.250 | 4x13.250 | 4x10.125 | 6x12.078 |  | 4x13.250 | 4x13.250 | 4x13.250 | 4x13.250 | 4x13.250 | 4x13.250 | 4x13.250 | 4x13.250 | 4x10.125 | 6x12.078
6x15.218 | 6x15.218 | 6 | 6 | 6 | 6 | 6 | 6 | 4x13.250 | 6x15.218 |  | 6x15.218 | 6x15.218 | 6 | 6 | 6 | 6 | 6 | 6 | 4x13.250 | 6x15.218
|  | 6x8.937 | 6x8.937 | 6x8.937 | 6x8.937 | 6x8.937 | 6x8.937 | [5 empty] | 6x8.937 | 6x8.937 | 6x8.937 | 6x8.937 | 6x8.937 | 6x8.937
|  | 6x12.078 | 6x12.078 | 6x12.078 | 6x12.078 | 6x12.078 | 6x12.078 | [5 empty] | 6x12.078 | 6x12.078 | 6x12.078 | 6x12.078 | 6x12.078 | 6x12.078
|  | 6x15.218 | 6x15.218 | 6x15.218 | 6x15.218 | 6x15.218 | 6x15.218 | [5 empty] | 6x15.218 | 6x15.218 | 6x15.218 | 6x15.218 | 6x15.218 | 6x15.218

## SlotDiffusers_Model (hidden)
AS210 - Custom Flow Adjusta-Slot Linear 1 Slot
AS215 - Custom Flow Adjusta-Slot Linear 1 1/2 Slots
AS220 - Custom Flow Adjusta-Slot Linear 2 Slot
AS225 - Custom Flow Adjusta-Slot Linear 2 1/2 Slot
AS230 - Custom Flow Adjusta-Slot Linear 3 Slot
ASP210 - Custom Flow Engineered Plenum For AS210
ASP215 - Custom Flow Engineered Plenum For AS215
ASP220 - Custom Flow Engineered Plenum For AS220
ASP225 - Custom Flow Engineered Plenum For AS225
ASP230 - Custom Flow Engineered Plenum For AS230
ASPI210 - Custom Flow Insulated Engineered Plenum For AS210
ASPI215 - Custom Flow Insulated Engineered Plenum For AS215
ASPI220 - Custom Flow Insulated Engineered Plenum For AS220
ASPI225 - Custom Flow Insulated Engineered Plenum For AS225
ASPI230 - Custom Flow Insulated Engineered Plenum For AS230
CF - Custom Flow
CFP - Custom Flow Plenum
CFT - Custom Flow Integrated T-Bar Module
JS210 - Custom Flow Jet-Slot Linear 1 Slot
JS215 - Custom Flow Jet-Slot Linear 1 1/2 Slot
JS220 - Custom Flow Jet-Slot Linear 2 Slot
JS225 - Custom Flow Jet-Slot Linear 2 1/2 Slot
JS230 - Custom Flow Jet-Slot Linear 3 Slot
JSP210 - Custom Flow Engineered Plenum For JS210
JSP215 - Custom Flow Engineered Plenum For JS215
JSP220 - Custom Flow Engineered Plenum For JS220
JSP225 - Custom Flow Engineered Plenum For JS225
JSP230 - Custom Flow Engineered Plenum For JS230
JSPI210 - Insulated Custom Flow Engineered Plenum For JS210
JSPI215 - Insulated Custom Flow Engineered Plenum For JS215
JSPI220 - Insulated Custom Flow Engineered Plenum For JS220
JSPI225 - Insulated Custom Flow Engineered Plenum For JS225
JSPI230 - Insulated Custom Flow Engineered Plenum For JS230
SDR100 - Linear Slot Return 1 Slot
SDR50 - Linear Slot Return 1/2 Slot
SDR75 - Linear Slot Return 3/4 Slot
SDS100 - Linear Slot Supply 1 Slot
SDS50 - Linear Slot Supply 1/2 Slot
SDS75 - Linear Slot Supply 3/4 Slot
TBD2100 - T-Bar Curved Extruded Blade 1 Slot
TBD2150 - T-Bar Curved Extruded Blade 1 1/2 Slot
TBD3100 - T-Bar Diffuser Ice-Tong Blades 1 Slot
TBD350 - T-Bar Diffuser Ice-Tong Blades 1/2 Slot
TBD375 - T-Bar Diffuser Ice-Tong Blades 3/4 Slot
TBD4100 - T-Bar Straight Blade 1 Slot
TBD4150 - T-Bar Straight Blade 1 1/2 Slot
TBD475 - T-Bar Straight Blade 3/4 Slot
TBD638 - High Induction T-Bar Supply Diffuser 3/8 Slot
TBD7 - T-Bar Supp Diff Vane Fixed Patt Control 3/4Slot
TBDI2100 - Insulated T-Bar Curved Extruded Blades 1 Slot
TBDI2150 - Insulated T-Bar Curved Extruded Blades 1 1/2 Sl
TBDI3100 - Insulat T-Bar Supp Diff Ice-Tong Blades 1 Slots
TBDI350 - Insul T-Bar Supp Diff Ice-Tong Blades 1/2 Slots
TBDI375 - Insul T-Bar Supply Diff Ice-Tong Blades 3/4Slots
TBDI4100 - Insul T-Bar Supp Diff Straight Blades 1 Slots
TBDI4150 - Insul T-Bar Supp Diff Straight Blade 1 1/2 Slot
TBDI475 - Insul T-Bar Supp Diff Straight Blades 3/4 Slots
TBDI638 - Insul T-Bar Supp Diff High Induction 3/8 Slots
TBDI6HC - Thermal Powered Auto-Changeover Heat/Cool Diffuser
TBDI7 - Insul T-Bar Supp Vane Fixed Patt Control 3/4Slot