Price Stainless Steel Louvered Grille

Division 23 – Heating, Ventilating, and Air Conditioning

Section 23 37 13 – Diffusers, Registers, and Grilles

The following specification is for a defined application. Price would be pleased to assist in developing a specification for your specific need.

PART 1 – GENERAL

  - Section includes:

- Stainless Steel Louvered Grille.

  - Related Requirements

- Section 01 30 00 – Administrative Requirements

- Section 01 40 00 – Quality Requirements

- Section 01 60 00 – Product Requirements

- Section 01 74 21 – Construction/Demolition Waste Management and Disposal

- Section 01 78 00  – Closeout Submittals

- Section 01 79 00 – Demonstration and Training

  - Reference Standards

- All referenced standards and recommended practices in this section pertain to the most recent publication thereof, including all addenda and errata.

1.04	Submittals

- See Section 01 30 00 – Administrative Requirements for submittal procedures.

- Product Data: Provide data indicating configuration, general assembly, and materials used in fabrication. Include catalog performance ratings that indicate airflow, and NC designation.

- Shop Drawings: Indicate configuration, general assembly, and materials used in fabrication.

- Project Record Documents:  Record actual locations of units and control components.

- Operation and Maintenance Data:  Include manufacturer's descriptive literature, operating instructions (if applicable), and maintenance and repair data.

- Warranty:  Submit manufacturer warranty and ensure forms have been completed in Owner's name and registered with manufacturer.

- Maintenance Materials:  Furnish the following for Owner's use in maintenance of project.

## 1.06	Quality Assurance

- Manufacturer Qualifications:  Company specializing in manufacturing the type of products specified in this section, with minimum ten years of documented experience.

## 1.07	Warranty

- See Section 01 7800 - Closeout Submittals, for additional warranty requirements.

- Provide 12 month manufacturer warranty from date of shipment of grilles and registers.

PART 2 – PRODUCTS

2.01	Stainless Steel Louvered Grille

- Basis of Design: Price Industries, Inc.

- Stainless Steel Louvered Supply Grille: Model 710, 720,

- Stainless Steel Louvered Return Grille: Model 730, 735, 710Z

2.02	Stainless Steel Louvered Supply Grille

- Description:

  - Furnish and install Price Model [710] or [720] stainless steel louvered supply grilles and registers of sizes and mounting types designated by the plans and air distribution schedule.

- Construction:

  - Grilles shall be fixed louver type, and shall have (select one):

    - One set of fully adjustable blades, with 3/4 inch on center blade spacing [Model 710].

    - Two sets of fully adjustable blades, with the second set behind the first set, and with 1/2 inch on center blade spacing [Model 720].

  - The grille’s front blade orientation shall be (select one), as indicated on the outlet schedule.

    - Front blades parallel to the long dimension.

    - Front blades parallel to the short dimension.

  - The blades, frame, and border shall be stainless steel construction.

  - The minimum grille size shall be six inches by four inches. The maximum one-piece grille size shall be 48 x 48 inches.

  - The grille shall be supplied with a mullion when nominal grille dimensions exceed 24 inches.

- Finish:

  - The grille frame finish shall be #4 polished stainless steel.

  - The grille blade finish shall be 2B stainless steel.

- Options:

  - Opposed Blade Damper:

    - The grille shall be supplied with a mill finish stainless steel (DSS) opposed blade damper.

  - Border Style:

    - The grille shall be suitable for sidewall mounting or T-bar lay-in mounting, complete with a border in the following style (select one):

      - 1-1/4 inch flat border.

      - 1 inch narrow border.

  - Mounting Frames:

    - The grille shall be supplied with a 3/8 inch flat border mounting frame.

  - Fastening:

    - The grille shall be supplied with the following fastening method (select one):

  - Countersunk screw holes complete with screws.

  - No screw holes.

2.03	Stainless Steel Louvered Return Grille

- Description:

- Furnish and install Price Model [730], [735], [710Z] stainless steel louvered return grilles and registers of sizes and mounting types designated by the plans and air distribution schedule.

- Construction:

- Grilles shall be fixed louver type, and shall have (select one):

      - One set of fixed blades at 45 degree deflection with 3/4 inch on center blade spacing [Model 730]

      - One set of fixed blades at 45 degree deflection with 1/2 inch on center blade spacing [Model 735].

      - One set of 0 degree deflection blades with 3/4 inch on center blade spacing [Model 710Z]

- The grilles front blade orientation shall be (select one), as indicated on the outlet schedule.

    - Front blades parallel to the long dimension.

    - Front blades parallel to the short dimension.

- The blades and border shall be stainless steel construction.

- The grille shall use a continuous length piano type hinge and quarter turn quick-release fasteners for access.

- The minimum grille size shall be six inches by four inches. The maximum one-piece grille size shall be 48 inches x 48 inches.

- The grille shall be supplied with a mullion when nominal grille dimensions exceed 20 inches.

- Finish:

- The grille face finish shall be #4 polished stainless steel.

- The grille blade finish shall be 2B stainless steel.

- Options:

- Opposed Blade Damper:

        - The register shall be supplied with a mill finish stainless steel (DSS) opposed blade damper.

- Border Style:

- The grille shall be suitable for surface or T-bar mounting.

- Mounting Frames:

- The grille shall be supplied with a 3/8 inch flat border mounting frame.

- Fastening:

- The grille shall be supplied with the following fastening method (select one):

- Countersunk screw holes complete with screws.

- No screw holes [default for T-bar installations].

- Insect Screen:

  - The grille shall be supplied with an 18 x16 aluminum mesh insect screen. [not available with damper option]

PART 3 – EXECUTION

3.01	Examination

- Verify that conditions are suitable for installation.

- Verify that field measurements are as shown on the drawings.

3.02 	Installation

- Install in accordance with manufacturer’s instructions.

- See drawings for the size(s) and locations of grilles and registers.

3.03 	Field Quality Control

- See Section 01 40 00 – Quality Requirements for additional requirements.

3.05 	Cleaning

- See Section 01 74 19 – Construction Waste Management and Disposal for additional requirements.

3.06 	Closeout Activities

- See Section 01 78 00 – Closeout Submittals for closeout documentation requirements.

- See Section 01 79 00 – Demonstration and Training for additional requirements.