Price J-Blade Stationary Louver (4” Deep, 43° Blade)

Division 08 – Openings

Section 08 91 19 – Fixed Louvers

The following specification is for a defined application. Price would be pleased to assist in developing a specification for your specific need.

# PART 1 – GENERAL

1.01   	Section includes:

A. 	Stationary Louvers.

# 1.02   	Reference Standards

- All referenced standards and recommended practices in this section pertain to the most recent publication thereof, including all addenda and errata.

- AAMA 611 – Voluntary Specification for Anodized Architectural Aluminum

- AAMA 2603 – Voluntary Specification, Performance Requirements and Test Procedures For Pigmented Organic Coatings on Aluminum Extrusions and Panels

- AAMA 2605 – Voluntary Specification, Performance Requirements and Test Procedures For Superior Performing Pigmented Organic Coatings on Aluminum Extrusions and Panels

- AMCA 500L – Laboratory Methods for Testing Louvers for Rating

- ASTM D7091 (formerly ASTM D1400) – Standard Practice for Nondestructive Measurement of Dry Film Thickness of Nonmagnetic Coatings Applied to Ferrous Metals and Nonmagnetic, Nonconductive Coatings Applied to Non-Ferrous Metals

# 1.03 	Submittals

- Product Data: Provide data indicating configuration, general assembly, and materials used in fabrication. Include catalog performance ratings.

- Shop Drawings: Indicate configuration, general assembly, and materials used in fabrication.

Project Record Documents:  Record actual locations of units and control components.

- Operation and Maintenance Data:  Include manufacturer's descriptive literature, operating instructions (if applicable), and maintenance and repair data (if applicable).

- Warranty:  Submit manufacturer warranty and ensure forms have been completed in Owner's name and registered with manufacturer.

# 1.04 	Quality Assurance

- Manufacturer Qualifications:  Company specializing in manufacturing the type of products specified in this section, with minimum ten years of documented experience.

# 1.05 	Warranty

- See Section 01 7800 - Closeout Submittals, for additional warranty requirements.

- Provide 12 month manufacturer warranty from date of shipment of louvers.

PART 2 – PRODUCTS

# Stationary Louver

- Basis of Design: Price Industries, Inc.

  - J-Blade Stationary Louver

- Description:

  - Furnish and install Price Model JE443 Architectural Blade Louver of size and shape indicated on the plans and/or as described in schedules.

  - Louver performance shall be based on tests and procedures in accordance with AMCA publication 500-L.

- Construction:

  - Louvers shall be constructed of 6063-T5 alloy extruded aluminum.

  - Louver blades and frames shall be minimum 0.081 inch wall thickness. Louver assemblies shall be 4 inches deep with 43-degree stationary “J” profile blades. Louvers shall be welded construction.

  - Louvers shall be designed to withstand a 25 pound per square foot.

  - Louvers shall be fitted with 1/2 inch x 0.051 inch flattened expanded aluminum bird screen. Bird screen shall be mounted on interior louver face.

JE443

-

1

v001

Louvers shall be supplied with a standard mill finish.

- Options:

  - Screen (select one):

    - Louvers shall be fitted with 1/2 inch x 0.051 inch flattened expanded aluminum bird screen. Bird screen shall be permanently secured to a formed aluminum frame and mounted on interior louver face.

    - Louvers shall be fitted with 18 x 16 square per inch, plain weave 0.011 inch diameter aluminum insect screen permanently secured to a formed aluminum frame and mounted on interior louver face.

  - Construction features (select all required):

    - Louvers shall be supplied with a 1.5 inch [0.5 inch, 1.0 inch, 2.0 inch, 2.5 inch, 3.0 inch, 3.5 inch, 4.0 inch] flanged frame.

    - Louvers shall be supplied with a continuous blade appearance and concealed mullions.

    - Each louver shall be fitted with [1 inch, 2 inch, 3 inch, 4 inch insulated] or [a non-insulated] aluminum blank-off panel.

  - Finish (select one):

    - Thermosetting acrylic based resin coating for standard duty architectural applications:

      - Louvers shall be factory finished-after-assembly with a thermosetting acrylic based resin coating. Resin coating shall be oven cured in accordance with the coating manufacturer’s instructions.

      - The coating system shall have a minimum dry film thickness of 0.8 mil in accordance with ASTM D7091.

      - The coating system product shall meet salt spray and hardness specifications of AAMA 2603.

    - Cured fluoropolymer based resin coating for weather protection in architectural applications:

      - Louvers shall be factory primed and finished-after-assembly with a fluoropolymer based resin coating. Primer and resin coating shall be oven cured in accordance with the coating manufacturer’s instructions.

      - The coating system shall have a minimum dry film thickness of 0.25 mil primer and 1.0 mil colour coat in accordance with ASTM D7091.

      - The coating system product shall meet salt spray and hardness specifications of AAMA 2605.

    - Cured fluoropolymer based resin coating (Kynar 500) for corrosive architectural applications:

JE443

-

2

v001

Louvers shall be factory primed and finished-after-assembly with a fluoropolymer based resin coating and clear topcoat. Primer, resin and topcoat coating shall be oven cured in accordance with the coating manufacturer’s instructions.

      - The coating system shall have a minimum dry film thickness of 0.25 mil primer, 1.0 mil colour coat and 0.6 mil clear topcoat in accordance with ASTM D7091.

      - The coating system product shall meet salt spray and hardness specifications of AAMA 2605.

    - Colour Anodized Coating – Anodized finish type 1:

      - Louvers shall receive an anodized colour finish [Light Bronze, Medium Bronze, Dark Bronze, Black] in accordance with AAMA 611. The finish shall be applied to chemically etched and pretreated aluminum with a minimum thickness of 0.4 – 0.7 mils.

    - Clear Anodized Coating – Anodized finish type 2:

- Louvers shall receive a clear anodized finish in accordance with AAMA 611. The finish shall be applied to chemically etched and pretreated aluminum with a minimum thickness of 0.4 - 0.7 mils.

PART 3 – EXECUTION

# 3.01 	Examination

- Verify that conditions are suitable for installation.

- Verify that field measurements are as shown on the drawings.

# 3.02  	Installation

- Install in accordance with manufacturer’s instructions.

- See drawings for the size(s) and locations of louvers.