Price Linear Fan Terminal – Electric Coil

# Division 23 – Heating, Ventilating, and Air Conditioning Section

# 23 36 16 – Variable Air Volume Units

The following specification is for a defined application. Price would be pleased to assist in developing a specification for your specific need.

PART 1 – GENERAL

  - Summary

- This section includes the following:

- Linear Fan Terminal – Electric Coil

1.02	Related Documents

- Section 01 30 00 – Administrative Requirements

- Section 01 40 00 – Quality Requirements

- Section 01 60 00 – Product Requirements

- Section 01 74 19 – Construction/Demolition Waste Management and Disposal

- Section 01 78 00 – Closeout Submittals

- Section 01 79 00 – Demonstration and Training

- Section 23 30 00 – HVAC Air Distribution

- Section 23 32 00 – Air Plenums and Chases

  - Reference Standards

- All referenced standards and recommended practices in this section pertain to the most recent publication thereof, including all addenda and errata.

- ASHRAE Standard 62.1 – Standards for Ventilation and Indoor Air Quality

- ASHRAE Standard 70 – Method of Testing the Performance of Air Outlets and Air Inlets

- IEC 60335 – International Standard for Household and Similar Electrical Appliances - Safety

- NFPA Standard 70A, Article 100 – National Electrical Code

- RoHS 3 – Restriction of Hazardous Substances in Electrical and Electronic Equipment

- UL 900 – Standard for Air Filter Units

- UL 2021 – UL Standard for Fixed and Location-Dedicated Electric Room Heaters

1.04	Administrative Requirements

A. 	Pre-installation Meeting:  Conduct a pre-installation meeting one week prior to the start of the work of this section; require attendance by all affected installers.

B. 	Sequencing: Ensure that utility connections are achieved in an orderly and efficient manner.

1.05	Submittals

- Product Data:

  - Provide data indicating configuration, general assembly, materials used in fabrication, rated capacities, and furnished specialties and accessories.

  - Include drawings indicating size, profiles and dimensional requirements of the linear floor grilles that are based on the specific system indicated.

  - Include catalog performance ratings that indicate airflow volume, initial pressure drops, sound performance, and throw, as tested in accordance with ASHRAE 70.

- Shop Drawings:  For each type of product indicated, include the following:

1. 	Equipment assemblies and indicated dimensions.

2.	Required clearances.

3.	Method of field assembly.

4.	Revit models.

- Coordination Drawings: Include floor plans, and other details, drawn to scale, one which the following items are shown and coordinated with each other, based on input from installers of the items involved:

  - Floor or underfloor-mounted items including;

    - Floor structure (floor tiles, concrete, etc.)

    - Floor finishing (carpet, tile, etc.)

    - Access panels

    - Electrical components

    - Plumbing

    - Networking components

    - Terminal Units and other HVAC components

- Operation and Maintenance Data:  Include manufacturer’s descriptive literature, operating instructions, maintenance schedules and repair data, and parts lists.

1.06	Quality Assurance

- Manufacturer Qualifications:  Company specializing in manufacturing the type of products specified in this section, with minimum ten years of documented experience.

- Product Listing Organization Qualifications:  An organization recognized by OSHA as a Nationally Recognized Testing Laboratory (NRTL) and acceptable to authorities having jurisdiction.

- Electrical Components, Devices and Accessories: Listed and labeled as defined in NFPA 70, Article 100 by a testing agency acceptable to authorities having jurisdiction and marked for intended use.

## 1.07		Warranty

- See Section 01 78 00 - Closeout Submittals, for additional warranty requirements.

- Provide 18 months manufacturer warranty from date of shipment for grilles and registers.

PART 2 – PRODUCTS

2.01	General

- Basis of Design: Price Industries, Inc.

- Linear Fan Terminal – Electric Coil [Price Model LFT-EC]

- General Product Information:

- Furnish and install Price model LFT-EC of the sizes and capacities indicated on the drawings or outlet schedule.

- Unit sizes shall be selected in accordance with ASHRAE guidelines and manufacturer’s literature.

- Manufacturers shall demonstrate that they have successfully supplied and installed underfloor HVAC products, as well as the computer modeling thereof for a minimum of 10 years.

- Manufacturers must be pre-qualified to bid based on the completion of a minimum of [xx] jobs in similar climates.

- Manufacturers shall provide a list of completed jobs and references.

Underfloor Air System Controls:

  - Air Grilles and diffusers specified for underfloor service shall incorporate the following requirements:

    - Airflow and throw heights shall decrease in response to lower space demands with flow-modulation of constant temperature plenum air. The flow-modulation technique shall be implemented to maximize stratification, leading to energy savings and increased thermal comfort.

  - Molex connector cable:

    - Plug-and-play plenum rated cables with molex connectors shall be used between devices.

    - The cable shall be constructed of ten (10) individually insulated wires wrapped in an insulated jacket.

    - The cables shall carry the fan speed and electric heater modulation control signals to each LFT.

    - Cable types shall be limited to no more than one type and connector per device to reduce complexity in wiring and future modifications

    - The cable shall be 15, 25, or 35 feet in length.

© Copyright Price Industries Limited 2024. All metric dimensions are soft conversion.

Imperial dimensions are converted to metric and rounded to the nearest millimeter. For more information visit priceindustries.com.

  - Linear Fan Terminal

- Description:

  - Furnish and install Price model LFT-EC (L x W x H) with the sizes, configurations and capacities indicated on the plans and air outlet schedule.

- Performance:

  - The manufacturer of the linear fan terminal shall provide performance data for air volume, initial pressure drop, and heating and cooling element performance.

  - Performance data published should be collected from testing completed for in floor applications that represent the intended application. Bare heating element data not tested within the convective trough should not be considered.

  - Air shall be delivered to the space without the use of nozzles.

  - All data must be tested in accordance with the most recent publication of ASHRAE 70.

- Construction:

  - The plenum shall be constructed of minimum 20 gauge steel.

  - The LFT-EC shall be ETL certified.

  - The plenum style shall be [select one]:

    - [F] – Flanged – order with 1000 style LFG

    - [NF] – Non-flanged – order with 125/187 style LFG

    - [FL] – Flared – order with RFG

  - The LFT-EC shall be supplied complete with two modular jacks for system connections and modular molex cable.

  - The plenum shall be [floor tile] or [pedestal] supported or supported by [leveling feet].

  - Removable end caps for continuous LFG and RFG integration.

  - Plenum to be provided with a plenum extrusion for the [FL] type selection.

  - The LFT-EC shall be equipped with side knockouts if needed.

  - The LFT-EC can be controlled by either Price supplied T-stats or BACnet.

- Controls:

  - The LFT-EC controls shall be supplied by [select one]:

    - [EHP] – Controls by Price

      - [INT] - All Controls Components Internal of Plenum

      - [EXT] - Controls in External Remote Enclosure (Daisy Chain drone LFT-ECs to single remote controls enclosure)

        - Number of daisy chained drone LFT-EC is determined based on power supply size within the remote enclosure

        - Power connection is hardwired through terminal block connection between remote enclosure and drone LFT-ECs with appropriately sized cable (cable is provided by others).

    - [FLD] – Field mounted controls by others

      - [INT] - All Controls Components Internal of Plenum

      - [EXT]- Controls in External Remote Enclosure (Daisy Chain drone LFT-ECs to single remote controls enclosure)

        - Number of daisy chained drone LFT-EC is determined based on power supply size within the remote enclosure

        - Power connection is hardwired through terminal block connection between remote enclosure and drone LFT-ECs with appropriately sized cable (cable is provided by others).

    - [FAC] – Controls supplied by others – factory mounted by Price

      - [INT] - All Controls Components Internal of Plenum

      - [EXT]- Controls in External Remote Enclosure (Daisy Chain drone LFT-ECs to single remote controls enclosure)

        - Number of daisy chained drone LFT-EC is determined based on power supply size within the remote enclosure

        - Power connection is hardwired through terminal block connection between remote enclosure and drone LFT-ECs with appropriately sized cable (cable is provided by others).

- Thermostat for [EHP] only [select one]:

  - [SENS] – Blank Face Thermostat

  - [DIAL] – Dial Set-Point Thermostat

  - [LCD] – LCD Thermostat

  - [MOT] – LCD with Motion Sensor Thermostat

  - [CO2H] – LCD with CO2 and Humidity Monitoring Thermostat

- Heaters:

  - The unit shall be supplied with electric heater:

    - Shall be supplied with an electric finned tubular heater constructed of stainless-steel tubing material and aluminum-zinc fins. Heaters are of UL construction and shall be equipped with over temperature protection through an automatic temperature reset switch that allows sensing throughout a continuous unit length. The thermal cutoff switch should be designed for sensitivity that allows a response to individual hot spots along the unit length. Disconnect switch is included

    - The electric heater element shall be mounted in the sheet metal plenum below the grille.

    - Maximum electric heater capacity shall be:

      - 1000 Watts [48-inch-long units]

      - 2000 Watts [72-inch-long units

      - 2500 Watts [96-inch-long units]

- EC Fan:

  - The LFT-EC shall be equipped with one (1), two (2) or three (3) fans based on the length selection.

  - The fan motor and motor shaft shall be directly connected to the fan.

  - The fan motor shall be low voltage 24VDC.

  - The fan motor will accept a 0-10V control signal.

  - Fans shall be provided with a protective fan grate.

- Mounting/Fastening:

  - Floor tile supported units shall be supplied with a 1/2-inch flange on all sides.

  - Pedestal supported units shall be supplied with 16 GA pedestal support brackets attached to the units.

  - Leveling feet could be used in trench applications for flat placement of the unit. Increases unit height by minimum 0”, maximum 1”.

  - Support pedestals shall be positioned without the use of tools.

  - Pedestal and pedestal heads shall be provided by others.

- Electrical Requirements:

  - The unit equipment wiring shall comply with the requirements of NFPA 70.

  - The units shall be ETL listed and compliant with UL2021 and CSA C22.2#46.

  - All high voltage electrical components shall be enclosed in a single control box.

- Finish:

  - The plenum shall be finished in black powder coat.

  - [FL] Flared plenum comes with a plenum extrusion with the extrusion finish to match the RFG finish selected (RFG ordered separate).

- Options [select all that apply]:

  - Unit Voltage

    - 120V-1

    - 208V-1

    - 240V-1

    - 277V-1

  - Safety disconnect switch:

    - Manually control the power supply to the unit.

  - Overflow Protection [OFS]

    - LFT-EC can be equipped with an optional overflow safety flow switch mounted on the drain pan.

  - Fan Filter:

    - 30 PPI foam air filter.

    - Shall comply with UL 900 and RoHS 3.

    - Washable.

    - Shall be securely attached to the fan grate.

# PART 3 - EXECUTION

## Examination

## Verify that conditions are suitable for installation.

## Verify that field measurements are as shown on the drawings.

## Installation

## Install the units in accordance with the manufacturer's instructions.

## Install underfloor fan powered units level and plumb. Maintain sufficient clearance for normal services, maintenance, or in accordance with construction drawings.

## Complete installation and startup checks according to manufacturer’s instructions and perform the following:

## Verify that inlet duct connections are as recommended by the manufacturer to achieve proper performance.

## Verify that any identification tags are visible.

## Verify locations of thermostats, humidistats, and other exposed control sensors with drawings and room details before installation.

  - Field Quality Control

- See Section 01 40 00 - Quality Requirements, for additional quality requirements.

  - Cleaning

- See Section 01 74 19 - Construction Waste Management and Disposal for additional cleaning requirements.

## 3.06 Closeout Activities

- See Section 01 78 00 - Closeout Submittals for closeout submittals.

- See Section 01 79 00 - Demonstration and Training for additional closeout requirements.