Price LV Linear Vane Diffusers

Division 23 – Heating, Ventilating, and Air Conditioning

Section 23 37 13 – Diffusers, Registers, and Grilles

The following specification is for a defined application. Price would be pleased to assist in developing a specification for your specific need.

PART 1 – GENERAL

  - Section includes:

- Linear Vane Diffusers

  - Related Requirements

- Section 01 30 00 – Administrative Requirements

- Section 01 40 00 – Quality Requirements

- Section 01 60 00 – Product Requirements

- Section 01 74 21 – Construction/Demolition Waste Management and Disposal

- Section 01 78 00  – Closeout Submittals

- Section 01 79 00 – Demonstration and Training

  - Reference Standards

- All referenced standards and recommended practices in this section pertain to the most recent publication thereof, including all addenda and errata.

- ASHRAE 70 – Method of Testing the Performance of Air Outlets and Air Inlets

- ASTM D610 – Standard Practice for Evaluating Degree of Rusting on Painted Steel Surfaces

- ASTM D714 – Test Method for Evaluating Degree of Blistering of Paints

- ASTM D1308 – Standard Test Method for Effect of Household Chemicals on Clear and Pigmented Organic Finishes

- ASTM D1654 – Standard Test Method for Evaluation of Painted or Coated Specimens Subjected to Corrosive Environments

- ASTM D4752 – Standard Practice for Measuring MEK Resistance of Ethyl Silicate (Inorganic) Zinc-Rich Primers by Solvent Rub

- NFPA 90A – Standard for the Installation of Air-Conditioning and Ventilating Systems

- UL/ULC – Underwriters Laboratories Fire Resistance Directory/Underwriters Laboratories of Canada Equipment and Materials Directory, if applicable.

1.04	Submittals

- See Section 01 30 00 – Administrative Requirements for submittal procedures.

- Product Data: Provide data indicating configuration, general assembly, and materials used in fabrication. Include catalog performance ratings that indicate airflow, and NC designation.

- Shop Drawings: Indicate configuration, general assembly, and materials used in fabrication.

- Project Record Documents:  Record actual locations of units and control components.

- Operation and Maintenance Data:  Include manufacturer's descriptive literature, operating instructions (if applicable), and maintenance and repair data.

- Warranty:  Submit manufacturer warranty and ensure forms have been completed in Owner's name and registered with manufacturer.

- Maintenance Materials:  Furnish the following for Owner's use in maintenance of project.

## 1.06	Quality Assurance

- Manufacturer Qualifications:  Company specializing in manufacturing the type of products specified in this section, with minimum ten years of documented experience.

## 1.07	Warranty

- See Section 01 7800 - Closeout Submittals, for additional warranty requirements.

- Provide 12 month manufacturer warranty from date of shipment of diffusers.

PART 2 – PRODUCTS

2.01	Manufacturer

- Basis of Design: Price Industries, Inc.

- One-way Deflection Linear Vane Diffusers: Model LV1

- Two-way Deflection Linear Vane Diffusers: Model LV2

2.02	One-way Deflection Linear Vane Diffusers

- Description:

  - Furnish and install Price model LV1 linear vane supply diffusers of the sizes, configurations and mounting types designated by the plans and air distribution schedule.

- Construction:

  - Diffusers shall be have fixed, extruded aluminum one-way deflection louvers, with a minimum vane depth of 1-3/8 inch.

  - The core assembly shall be of mandrel tube construction and shall be removable from the outer border for installation.

  - The diffuser border shall be heavy extruded aluminum construction.

  - Diffusers supplied in multiple sections will include open ends at each section joint for continuous appearance, and finished endcaps at either end.

  - Alignment pins shall be provided to align continuous length assemblies.

- Paint Specification:

  - Paint finish shall be (select one):

    - Baked-on powder coat finish.

      - The paint film thickness shall be a minimum of 2 mils.

      - The finish shall have a hardness of 2H as tested in accordance with ASTM D3363.

      - The finish shall pass an ASTM B117 Corrosive Environment Salt Spray Test for 1000 hours with no measurable creep, rusting or blistering as per ASTM D1654, D610 and D714.

      - The finish shall pass an ASTM D870 Water Immersion test of a minimum of 500 hours with no measurable with no rusting or blistering as per ASTM D610 and D714.

      - The finish shall have an impact resistance of 100 inch-pounds in accordance with ASTM D2794.

    - All components shall have a custom finish in a color to match a customer supplied sample.

- Options (select all that apply):

  - Directional Vanes:

    - The diffuser shall be provided with rear-mounted, individually adjustable extruded aluminum blades spaced 1 inch on center for directional and spread control.

  - Damper:

    - The diffuser shall be supplied with an integral opposed blade type volume control damper with coated [cold rolled steel] or [aluminum] construction.

2.03	Two-way Deflection Linear Vane Diffusers

- Description:

  - Furnish and install Price model LV2 linear vane supply diffusers of the sizes, configurations and mounting types designated by the plans and air distribution schedule.

- Construction:

  - Diffusers shall be have fixed, extruded aluminum two-way deflection louvers, with a minimum vane depth of 1-3/8 inch.

  - The core assembly shall be of mandrel tube construction and shall be removable from the outer border for installation.

  - The diffuser border shall be heavy extruded aluminum construction.

  - Diffusers supplied in multiple sections will include open ends at each section joint for continuous appearance, and finished endcaps at either end.

  - Alignment pins shall be provided to align continuous length assemblies.

- Paint Specification:

  - Paint finish shall be (select one):

    - Baked-on powder coat finish.

      - The paint film thickness shall be a minimum of 2 mils.

      - The finish shall have a hardness of 2H as tested in accordance with ASTM D3363.

      - The finish shall pass an ASTM B117 Corrosive Environment Salt Spray Test for 1000 hours with no measurable creep, rusting or blistering as per ASTM D1654, D610 and D714.

      - The finish shall pass an ASTM D870 Water Immersion test of a minimum of 500 hours with no measurable with no rusting or blistering as per ASTM D610 and D714.

      - The finish shall have an impact resistance of 100 inch-pounds in accordance with ASTM D2794.

    - All components shall have a custom finish in a color to match a customer supplied sample.

- Options (select all that apply):

  - Directional Vanes:

    - The diffuser shall be provided with rear mounted, individually adjustable extruded aluminum blades spaced 1 inch on center for directional and spread control.

  - Damper:

    - The diffuser shall be supplied with an integral opposed blade type volume control damper with coated [cold rolled steel] or [aluminum] construction.

PART 3 – EXECUTION

3.01	Examination

- Verify that conditions are suitable for installation.

- Verify that field measurements are as shown on the drawings.

3.02 	Installation

- Install in accordance with manufacturer’s instructions.

- See drawings for the size(s) and locations of diffusers.

3.03 	Field Quality Control

- See Section 01 40 00 – Quality Requirements for additional requirements.

3.05 	Cleaning

- See Section 01 74 19 – Construction Waste Management and Disposal for additional requirements.

3.06 	Closeout Activities

- See Section 01 78 00 – Closeout Submittals for closeout documentation requirements.

- See Section 01 79 00 – Demonstration and Training for additional requirements.