Price Security Perforated Face Grille

Division 23 – Heating, Ventilating, and Air Conditioning

Section 23 37 13 – Diffusers, Registers, and Grilles

The following specification is for a defined application. Price would be pleased to assist in developing a specification for your specific need.

PART 1 – GENERAL

  - Section includes:

Security Grille with Perforated Face.

  - Related Requirements

- Section 01 30 00 – Administrative Requirements

Section 01 40 00 – Quality Requirements

Section 01 60 00 – Product Requirements

Section 01 74 21 – Construction/Demolition Waste Management and Disposal

Section 01 78 00  – Closeout Submittals

Section 01 79 00 – Demonstration and Training

  - Reference Standards

- All referenced standards and recommended practices in this section pertain to the most recent publication thereof, including all addenda and errata.

ASTM D610 – Standard Practice for Evaluating Degree of Rusting on Painted Steel Surfaces

ASTM D714 – Test Method for Evaluating Degree of Blistering of Paints

ASTM D870 – Standard Practice for Testing Water Resistance of Coatings Using Water Immersion

ASTM D1654 – Standard Test Method for Evaluation of Painted or Coated Specimens Subjected to Corrosive Environments

ASTM D2794 – Standard Test Method for Resistance of Organic Coatings to the Effects of Rapid Deformation (Impact)

ASTM D3363 – Standard Test Method for Film Hardness by Pencil Test

1.04	Submittals

- See Section 01 30 00 – Administrative Requirements for submittal procedures.

Product Data: Provide data indicating configuration, general assembly, and materials used in fabrication. Include catalog performance ratings that indicate air flow, and NC designation.

Shop Drawings: Indicate configuration, general assembly, and materials used in fabrication.

Project Record Documents:  Record actual locations of units and control components.

Operation and Maintenance Data:  Include manufacturer's descriptive literature, operating instructions (if applicable), and maintenance and repair data.

Warranty:  Submit manufacturer warranty and ensure forms have been completed in Owner's name and registered with manufacturer.

Maintenance Materials:  Furnish the following for Owner's use in maintenance of project.

## 1.06	Quality Assurance

- Manufacturer Qualifications:  Company specializing in manufacturing the type of products specified in this section, with minimum ten years of documented experience.

## 1.07	Warranty

- See Section 01 7800 - Closeout Submittals, for additional warranty requirements.

- Provide 12 month manufacturer warranty from date of shipment of grilles and registers.

PART 2 – PRODUCTS

2.01	Security Grilles with Perforated Face

- Basis of Design: Price Industries, Inc.

  - Security Perforated Face Grille: Model MSPG

2.02	Security Perforated Face Grille

- Description:

  - Furnish and install Price Model MSPG security perforated face grilles of sizes and mounting types designated by the plans and air distribution schedule.

- Construction:

  - The grilles shall be [3/16 inch thick], [10 gauge] or [12 gauge] and be made of (select one):

    - Steel

    - Aluminum

    - Stainless Steel

  - The grille face will have the following perforated pattern (select one):

    - P1 with 5/16 inch diameter holes staggered on 7/16 inch centers

    - P2 with 3/16 inch diameter holes staggered on 5/16 inch centers

    - P3 with ¼ inch diameter holes staggered on 3/8 centers

    - P4 with 7/16 inch diameter holes staggered on 11/16 centers

    - P5 with 1/8inch diameter holes staggered on 3/16 centers. Accepted by New York State Office of Mental Health. See NYS-OMH Patient safety Standards for Guidelines.

  - The grille face shall be fastened to a [3/16 inch thick], [10 gauge] or [12 gauge] wall sleeve.

- Paint Specification:

  - Paint finish shall be (select one):

    - Baked-on powder coat finish.

      - The paint film thickness shall be a minimum of 2 mils.

      - The finish shall have a hardness of 2H as tested in accordance with ASTM D3363.

      - The finish shall pass an ASTM B117 Corrosive Environment Salt Spray Test for 1000 hours with no measurable creep, rusting or blistering as per ASTM D1654, D610 and D714.

      - The finish shall pass an ASTM D870 Water Immersion test of a minimum of 500 hours with no measurable with no rusting or blistering as per ASTM D610 and D714.

      - The finish shall have an impact resistance of 100 inch-pounds in accordance with ASTM D2794.

    - All components shall have a custom finish in a color to match a customer supplied sample.

    - All stainless steel components shall be 2B stainless steel.

- Options (select all that apply):

  - Sleeve Construction (select one):

    - The sleeve shall be stitch welded.

    - The sleeve shall be continuously welded.

  - Fastening option (select one):

    - The grille shall be supplied with a 1 x 1 x 3/16 inch steel angle mounting frames.

    - The grille shall be supplied with a 1-1/2 x 1-1/2 x 3/16 inch steel angle mounting frames.

    - The grille shall be supplied with a 1 x 1 x 1/8 inch steel angle mounting frames.

    - The grille shall be supplied with a 1-1/2 x 1-1/2 x 1/8 inch steel angle mounting frames.

    - 3/4 inch diameter x 3 inch masonry rods.

    - Countersunk #12 plated steel spanner screws.

    - Countersunk #12 stainless steel spanner screws.

    - Countersunk #12 plated steel Torx screws.

    - Countersunk #12 stainless steel Torx screws.

  - Damper:

    - The grille shall be supplied with a front operated opposed blade damper

  - Barrier bars (select one):

    - The grille shall be supplied with ½ inch diameter hot rolled steel barrier bars

    - The grille shall be supplied with 3/4 inch diameter hot rolled steel barrier bars

    - The grille shall be supplied with ½ inch diameter hardened steel barrier bars in sockets

    - The grille shall be supplied with 3/4 inch diameter hardened steel barrier bars in sockets

    - The grille shall be supplied with 2 x ¼ inch flat hot rolled steel bars

  - Wire Mesh:

    - The grille shall be supplied with 10 gauge 3/8 inch clear opening steel mesh.

  - Transfer grille:

    - The grille shall be supplier with a matching welded rear plate.

PART 3 – EXECUTION

3.01	Examination

- Verify that conditions are suitable for installation.

- Verify that field measurements are as shown on the drawings.

3.02 	Installation

- Install in accordance with manufacturer’s instructions.

- See drawings for the size(s) and locations of grilles and registers.

3.03 	Field Quality Control

- See Section 01 40 00 – Quality Requirements for additional requirements.

3.05 	Cleaning

- See Section 01 74 19 – Construction Waste Management and Disposal for additional requirements.

3.06 	Closeout Activities

- See Section 01 78 00 – Closeout Submittals for closeout documentation requirements.

- See Section 01 79 00 – Demonstration and Training for additional requirements.