Price Risk Resistant Security Grille with Louvered Face

Division 23 – Heating, Ventilating, and Air Conditioning

Section 23 37 13 – Diffusers, Registers, and Grilles

The following specification is for a defined application. Price would be pleased to assist in developing a specification for your specific need.

PART 1 – GENERAL

  - Section includes:

- Security Grille with Perforated Face.

  - Related Requirements

- Section 01 30 00 – Administrative Requirements

- Section 01 40 00 – Quality Requirements

- Section 01 60 00 – Product Requirements

- Section 01 74 21 – Construction/Demolition Waste Management and Disposal

- Section 01 78 00  – Closeout Submittals

- Section 01 79 00 – Demonstration and Training

  - Reference Standards

- All referenced standards and recommended practices in this section pertain to the most recent publication thereof, including all addenda and errata.

- ASTM 610 – Standard Practice for Evaluating Degree of Rusting on Painted Steel Surfaces

- ASTM 714 – Test Method for Evaluating Degree of Blistering of Paints

- ASTM A627 – Standard Test Methods for Tool-Resisting Steel Bars, Flats, and Shapes for Detention and Correctional Facilities

- ASTM D1308 – Standard Test Method for Effect of Household Chemicals on Clear and Pigmented Organic Finishes

- ASTM D1654 – Standard Test Method for Evaluation of Painted or Coated Specimens Subjected to Corrosive Environments

- ASTM D4752 – Standard Practice for Measuring MEK Resistance of Ethyl Silicate (Inorganic) Zinc-Rich Primers by Solvent Rub

1.04	Submittals

- See Section 01 30 00 – Administrative Requirements for submittal procedures.

- Product Data: Provide data indicating configuration, general assembly, and materials used in fabrication. Include catalog performance ratings that indicate air flow, and NC designation.

- Shop Drawings: Indicate configuration, general assembly, and materials used in fabrication.

- Project Record Documents:  Record actual locations of units and control components.

- Operation and Maintenance Data:  Include manufacturer's descriptive literature, operating instructions (if applicable), and maintenance and repair data.

- Warranty:  Submit manufacturer warranty and ensure forms have been completed in Owner's name and registered with manufacturer.

- Maintenance Materials:  Furnish the following for Owner's use in maintenance of project.

## 1.06	Quality Assurance

- Manufacturer Qualifications:  Company specializing in manufacturing the type of products specified in this section, with minimum ten years of documented experience.

## 1.07	Warranty

- See Section 01 7800 - Closeout Submittals, for additional warranty requirements.

- Provide 12 month manufacturer warranty from date of shipment of grilles and registers.

PART 2 – PRODUCTS

2.01	Risk Resistant Security Grille with Louvered Core

- Basis of Design: Price Industries, Inc.

- Maximum Security Risk Resistant Grille with Louvered Core: MSRRG

2.02	Maximum Security Risk Resistant Grille with Louvered Core

- Description:

  - Furnish and install Price Model MSRRG security louvered face grilles of sizes and mounting types designated by the plans and air distribution schedule.

- Construction:

  - The grille shall be hot rolled steel construction, consisting of a 3/16 inch thick face plate.

  - The grille shall have 1” louvers at a 45 degree angle on ¼ inch centers with 12 gauge 1 ¾ inch hot rolled steel bars piercing the louvers on ½” centers.

  - The grille face shall be fastened to a [3/16 inch thick], [1/4 inch thick], [10 gauge] or [12 gauge] wall sleeve

- Paint Specification:

  - The grille paint finish shall be (select one):

    - All steel components shall have a baked-on powder coat finish.

      - The paint finish must demonstrate no degradation when tested in accordance with ASTM D1308 (covered and spot immersion) and ASTM D4752 (MEK double rub) paint durability tests.

      - The paint film thickness shall be a minimum of 2.0 mils.

      - The finish shall have a hardness of 2H.

      - The finish shall withstand a minimum salt spray exposure of 1000 hours with no measurable creep in accordance with ASTM D1654, and 1000 hours of exposure with no rusting or blistering as per ASTM D610 and ASTM D714.

      - The finish shall have an impact resistance of 80 inch-pounds.

    - All steel components shall have a custom finish in a color to match a customer supplied sample.

- Options:

  - Sleeve Construction (select one):

    - The sleeve shall be stitch welded.

    - The sleeve shall be continuously welded.

    - The sleeve shall have a bent out rear flange.

  - Mounting Frame (select one):

    - The grille shall be supplied with a 1 x 1 x 3/16 inch steel angle mounting frames.

    - The grille shall be supplied with a 1-1/2 x 1-1/2 x 3/16 inch steel angle mounting frames.

    - The grille shall be supplied with a 1 x 1 x 1/8 inch steel angle mounting frames.

    - The grille shall be supplied with a 1-1/2 x 1-1/2 x 1/8 inch steel angle mounting frames.

  - Fastening:

    - The grille shall be supplied with the following fastening method (select one):

  - 3/4 inch diameter x 3 inch masonry rods.

  - 3/4 inch diameter x 3 inch bent out masonry rods.

  - Countersunk #12 plated steel spanner screws

  - Countersunk #12 stainless steel spanner screws

  - Countersunk #12 plated steel Torx screws

  - Countersunk #12 stainless steel Torx screws

  - Damper:

    - The grille shall be supplier with a rear operated opposed blade damper

  - Barrier bars (select one):

    - The grille shall be supplied with ½ inch diameter hot rolled steel barrier bars

    - The grille shall be supplied with 3/4 inch diameter hot rolled steel barrier bars

    - The grille shall be supplied with 1 inch diameter hot rolled steel barrier bars

    - The grille shall be supplied with ½ inch diameter hardened steel barrier bars in sockets

    - The grille shall be supplied with 3/4 inch diameter hardened steel barrier bars in sockets

    - The grille shall be supplied with 1 inch diameter hardened steel barrier bars in sockets

    - The grille shall be supplied with 2 x ¼ inch flat hot rolled steel bars

    - The grille shall be supplied with vertical ¾ inch diameter hot rolled steel bars and horizontal 2 x ¼ inch flat bars

PART 3 – EXECUTION

3.01	Examination

- Verify that conditions are suitable for installation.

- Verify that field measurements are as shown on the drawings.

3.02 	Installation

- Install in accordance with manufacturer’s instructions.

- See drawings for the size(s) and locations of grilles and registers.

3.03 	Field Quality Control

- See Section 01 40 00 – Quality Requirements for additional requirements.

3.05 	Cleaning

- See Section 01 74 19 – Construction Waste Management and Disposal for additional requirements.

3.06 	Closeout Activities

- See Section 01 78 00 – Closeout Submittals for closeout documentation requirements.

- See Section 01 79 00 – Demonstration and Training for additional requirements.