Price Four Way Linear Slot Diffusers

Division 23 – Heating, Ventilating, and Air Conditioning

Section 23 37 13 – Diffusers, Registers, and Grilles

The following specification is for a defined application. Price would be pleased to assist in developing a specification for your specific need.

PART 1 – GENERAL

  - Section includes:

- Four-Way Linear Slot Diffusers

  - Related Requirements

- Section 01 30 00 – Administrative Requirements

- Section 01 40 00 – Quality Requirements

- Section 01 74 21 – Construction/Demolition Waste Management and Disposal

- Section 01 78 00  – Closeout Submittals

- Section 01 79 00 – Demonstration and Training

  - Reference Standards

- All referenced standards and recommended practices in this section pertain to the most recent publication thereof, including all addenda and errata.

- ASHRAE 70 – Standard Method of Testing the Performance of Air Outlets and Air Inlets

- ASTM D610 – Standard Practice for Evaluating Degree of Rusting on Painted Steel Surfaces

- ASTM D714 – Standard Test Method for Evaluating Degree of Blistering of Paints

- ASTM D1308 – Standard Test Method for Effect of Household Chemicals on Clear and Pigmented Organic Finishes

- ASTM D1654 – Standard Test Method for Evaluation of Painted or Coated Specimens Subjected to Corrosive Environments

- ASTM D4752 – Standard Practice for Measuring MEK Resistance of Ethyl Silicate (Inorganic) Zinc-Rich Primers by Solvent Rub

1.04	Submittals

- See Section 01 30 00 – Administrative Requirements for submittal procedures.

- Product Data: Provide data indicating configuration, general assembly, and materials used in fabrication. Include catalog performance ratings that indicate airflow, and NC designation.

- Shop Drawings: Indicate configuration, general assembly, and materials used in fabrication.

- Project Record Documents:  Record actual locations of units and control components.

- Operation and Maintenance Data:  Include manufacturer's descriptive literature, operating instructions (if applicable), and maintenance and repair data.

- Warranty:  Submit manufacturer warranty and ensure forms have been completed in Owner's name and registered with manufacturer.

- Maintenance Materials:  Furnish the following for Owner's use in maintenance of project.

## 1.06	Quality Assurance

- Manufacturer Qualifications:  Company specializing in manufacturing the type of products specified in this section, with minimum ten years of documented experience.

## 1.07	Warranty

- See Section 01 78 00 - Closeout Submittals, for additional warranty requirements.

- Provide 12 month manufacturer warranty from date of shipment of diffusers.

PART 2 – PRODUCTS

2.01	Manufacturer

- Basis of Design: Price Industries, Inc.

- Four-Way Linear Slot Supply Diffusers: Model SDS4

- Four-Way Linear Slot Return Diffusers: Model SDR4

2.02	Four-Way Linear Slot Supply Diffusers

- Description:

  - Furnish and install Price model SDS4 four-way linear slot supply diffusers in the capacities as shown by the plans and air distribution schedule.

- Construction:

  - The diffusers shall be a 24 inch by 24 inch module with [1 to 4] discharge slots, [1/2 inch], [3/4 inch], or [1 inch] slot width, and a round inlet.

  - The diffuser frame and slot spacers shall be extruded aluminum construction.

  - The supply diffusers shall have aerodynamically curved “ice-tong” shaped pattern controllers allowing for individual slot adjustment. The pattern controllers shall be fully adjustable, providing [one-way], [two-way], [two-way corner], [three-way], or [four-way] flow pattern control with a stable horizontal air pattern. All adjustments shall be accessible from the face of the diffuser.

  - The diffuser shall have a ceiling tile (supplied by others) cut and placed in the face of the diffuser. The ceiling tile shall match the surrounding ceiling system.

  - The linear slot diffusers shall be compatible for T-bar lay in mounting with the following border style (select one):

    - Inverted T-bar, 15/16 inch lay-in flush frame.

    - Narrow member T-bar, 9/16 inch x 5/16 inch width.

- Paint Specification:

  - Paint finish shall be (select one):

    - Baked-on powder coat finish.

      - The paint film thickness shall be a minimum of 2 mils.

      - The finish shall have a hardness of 2H as tested in accordance with ASTM D3363.

      - The finish shall pass an ASTM B117 Corrosive Environment Salt Spray Test for 1000 hours with no measurable creep, rusting or blistering as per ASTM D1654, D610 and D714.

      - The finish shall pass an ASTM D870 Water Immersion test of a minimum of 500 hours with no measurable with no rusting or blistering as per ASTM D610 and D714.

      - The finish shall have an impact resistance of 100 inch-pounds in accordance with ASTM D2794.

    - All components shall have a custom finish in a color to match a customer supplied sample.

    - The diffuser shall have an anodized finish.

2.03	Four-Way Linear Slot Return Diffusers

- Description:

  - Furnish and install Price model SDR4 four-way linear slot return diffusers in the capacities as shown by the plans and air distribution schedule.

- Construction:

  - The diffusers shall be a 24 inch by 24 inch module with [1 to 4] slots, and [1/2 inch], [3/4 inch], or [1 inch] slot width, and shall match the supply SDS4 diffusers in appearance.

  - The diffuser frame and slot spacers shall be extruded aluminum construction.

  - The diffuser shall have a ceiling tile (supplied by others) cut and placed in the face of the diffuser. The ceiling tile shall match the surrounding ceiling system.

  - The linear slot diffusers shall be compatible for T-bar lay in mounting with the following border style (select one):

    - Inverted T-bar, 15/16 inch lay-in flush frame.

    - Narrow member T-bar, 9/16 inch x 5/16 inch width.

- Paint Specification:

  - Paint finish shall be (select one):

    - Baked-on powder coat finish.

      - The paint film thickness shall be a minimum of 2 mils.

      - The finish shall have a hardness of 2H as tested in accordance with ASTM D3363.

      - The finish shall pass an ASTM B117 Corrosive Environment Salt Spray Test for 1000 hours with no measurable creep, rusting or blistering as per ASTM D1654, D610 and D714.

      - The finish shall pass an ASTM D870 Water Immersion test of a minimum of 500 hours with no measurable with no rusting or blistering as per ASTM D610 and D714.

      - The finish shall have an impact resistance of 100 inch-pounds in accordance with ASTM D2794.

    - All components shall have a custom finish in a color to match a customer supplied sample.

    - The diffuser shall have an anodized finish.

PART 3 – EXECUTION

3.01	Examination

- Verify that conditions are suitable for installation.

- Verify that field measurements are as shown on the drawings.

3.02 	Installation

- Install in accordance with manufacturer’s instructions.

- See drawings for the size(s) and locations of diffusers.

3.03 	Field Quality Control

- See Section 01 40 00 – Quality Requirements for additional requirements.

3.05 	Cleaning

- See Section 01 74 19 – Construction Waste Management and Disposal for additional requirements.

3.06 	Closeout Activities

- See Section 01 78 00 – Closeout Submittals for closeout documentation requirements.

- See Section 01 79 00 – Demonstration and Training for addition.