Price UP Universal Plenum

Division 23 – Heating, Ventilating, and Air Conditioning

Section 23 37 13 – Diffusers, Registers, and Grilles

The following specification is for a defined application. Price would be pleased to assist in developing a specification for your specific need.

PART 1 – GENERAL

  - Section includes:

- Universal Plenum

  - Related Requirements

- Section 01 30 00 – Administrative Requirements

- Section 01 40 00 – Quality Requirements

- Section 01 60 00 – Product Requirements

- Section 01 74 21 – Construction/Demolition Waste Management and Disposal

- Section 01 78 00  – Closeout Submittals

- Section 01 79 00 – Demonstration and Training

  - Reference Standards

- All referenced standards and recommended practices in this section pertain to the most recent publication thereof, including all addenda and errata.

- ASTM 610 – Standard Practice for Evaluating Degree of Rusting on Painted Steel Surfaces

- ASTM 714 – Test Method for Evaluating Degree of Blistering of Paints

- ASTM D1308 – Standard Test Method for Effect of Household Chemicals on Clear and Pigmented Organic Finishes

- ASTM D1654 – Standard Test Method for Evaluation of Painted or Coated Specimens Subjected to Corrosive Environments

- ASTM D4752 – Standard Practice for Measuring MEK Resistance of Ethyl Silicate (Inorganic) Zinc-Rich Primers by Solvent Rub

1.04	Submittals

- See Section 01 30 00 – Administrative Requirements for submittal procedures.

- Product Data: Provide data indicating configuration, general assembly, and materials used in fabrication. Include catalog performance ratings that indicate airflow, and NC designation.

- Shop Drawings: Indicate configuration, general assembly, and materials used in fabrication.

- Project Record Documents:  Record actual locations of units and control components.

- Operation and Maintenance Data:  Include manufacturer's descriptive literature, operating instructions (if applicable), and maintenance and repair data.

- Warranty:  Submit manufacturer warranty and ensure forms have been completed in Owner's name and registered with manufacturer.

- Maintenance Materials:  Furnish the following for Owner's use in maintenance of project.

## 1.06	Quality Assurance

- Manufacturer Qualifications:  Company specializing in manufacturing the type of products specified in this section, with minimum ten years of documented experience.

## 1.07	Warranty

- See Section 01 7800 - Closeout Submittals, for additional warranty requirements.

- Provide 12 month manufacturer warranty from date of shipment of diffusers.

PART 2 – PRODUCTS

2.01	Manufacturer

- Basis of Design: Price Industries, Inc.

- Universal Plenum: Models UP, UPL

- Curved Universal Plenum: Models UPC, UPLC

2.02	Universal Plenum

- Description:

  - Furnish and install Price Model [UP] or [UPL] universal plenum of the sizes indicated on the plans and air distribution schedule.

- Construction:

  - The plenum shall be constructed of zinc coated steel.

  - The plenum shall have a round inlet and the overall plenum height shall not exceed the diameter of the round inlet plus four inches. The inlet shall include a 1-1/4 inch flange for connecting to ductwork.

  - The open edge of the plenum shall have a hemmed edge for installation of a [concealed mounting bracket] or [straight edge] sized to fit the specified linear [diffuser] or [grille].

  - Maximum width shall be 24 inches.

- Application:

  - The universal plenum shall be used for the following diffuser application (select one):

    - Price Custom Flow Diffuser, Model CF

    - Price Linear Bar Grille, Model LBP

    - Price Supply/Return Slot Diffuser, Model SDS

- Paint Specification:

  - Paint finish shall be:

    - Coated steel.

- Options:

  - Damper:

    - The diffuser shall be supplied with a galvanized steel, cable operated volume control damper.

  - Low Profile (Model UPL):

    - The plenum shall have an oval inlet and overall plenum height shall not exceed 9 inches. The inlet shall include a 1-1/4 inch flange for connecting to ductwork.

    - The maximum with for a low profile height plenum shall be 12 inches.

  - Insulation:

    - The plenum shall be insulated with 1/4 inch thick insulation. Internally insulated plenums shall be oversized to maintain open free area inside the plenum.

    - The insulation shall be (select one):

      - Coated fiberglass, internally insulated.

      - Fiber free foam liner, internally insulated.

      - Aluminum foil backed fiberglass board, externally insulated.

2.03	Curved Universal Plenum

- Description:

  - Furnish and install Price Model [UPC] or [UPLC] curved universal plenum of the sizes indicated on the plans and air distribution schedule.

- Construction:

- The plenum shall be constructed of zinc coated steel.

- The plenum shall have a round inlet and the overall plenum height shall not exceed the diameter of the round inlet plus four inches. The inlet shall include a 1-1/4 inch flange for connecting to ductwork.

- The inlet location shall be toward the [inside] or [outside] of the curvature.

- The curved plenum shall be constructed with a [flat face], [convex], or [concave] curve.

- The minimum curve inside radius shall be [120 inches for CFC], [72 inches for SDC].

- Application:

  - The universal plenum shall be used for the following diffuser application (select one):

    - Price Curved Custom Flow diffuser, Model CFC.

    - Price Curved Linear bar grille, Model LBPC.

    - Price Curved Supply/Return Slot Diffuser, Model SDC.

- Paint Specification:

- Paint finish shall be:

    - Coated steel.

- Options:

  - Hemmed Sidewall:

    - For surface mount applications, the curved plenum shall be supplied with a 1/4 inch hemmed edge for installation of a [concealed mounting bracket] or [straight edge] sized to fit the specified linear [diffuser] or [grille].

    - For lay-in ceiling applications, the curved plenum shall be supplied with a flat sidewall sized to fit the specified linear [diffuser] or [grille].

  - Damper:

    - The diffuser shall be supplied with a galvanized steel, cable operated volume control damper.

  - Low Profile (Model UPLC):

    - The plenum shall have an oval inlet and overall plenum height shall not exceed 9 inches. The inlet shall include a 1-1/4 inch flange for connecting to ductwork.

    - The maximum with for a low profile height plenum shall be 12 inches.

  - Insulation:

  - The plenum shall be internally insulated with 1/4 inch thick insulation. Internally insulated plenums shall be oversized to maintain open free area inside the plenum.

  - The insulation shall be (select one):

      - Coated fiberglass.

      - Fiber free foam liner.

PART 3 – EXECUTION

3.01	Examination

- Verify that conditions are suitable for installation.

- Verify that field measurements are as shown on the drawings.

3.02 	Installation

- Install in accordance with manufacturer’s instructions.

- See drawings for the size(s) and locations of diffusers.

3.03 	Field Quality Control

- See Section 01 40 00 – Quality Requirements for additional requirements.

3.05 	Cleaning

- See Section 01 74 19 – Construction Waste Management and Disposal for additional requirements.

3.06 	Closeout Activities

- See Section 01 78 00 – Closeout Submittals for closeout documentation requirements.

- See Section 01 79 00 – Demonstration and Training for additional requirements.