Price Perforated Return

Division 23 – Heating, Ventilating, and Air Conditioning

Section 23 37 13 – Diffusers, Registers, and Grilles

The following specification is for a defined application. Price would be pleased to assist in developing a specification for your specific need.

PART 1 – GENERAL

  - Section includes:

- Perforated Return

  - Related Requirements

- Section 01 30 00 – Administrative Requirements

- Section 01 40 00 – Quality Requirements

- Section 01 74 21 – Construction/Demolition Waste Management and Disposal

- Section 01 78 00  – Closeout Submittals

- Section 01 79 00 – Demonstration and Training

  - Reference Standards

- All referenced standards and recommended practices in this section pertain to the most recent publication thereof, including all addenda and errata.

- ASHRAE Standard 55 – Thermal Environmental Conditions for Human Occupancy

- ASHRAE Standard 70 – Method of Testing the Performance of Air Outlets and Air Inlets

- ASTM 610 – Standard Practice for Evaluating Degree of Rusting on Painted Steel Surfaces

- ASTM 714 – Test Method for Evaluating Degree of Blistering of Paints

- ASTM D1308 – Standard Test Method for Effect of Household Chemicals on Clear and Pigmented Organic Finishes

- ASTM D1654 – Standard Test Method for Evaluation of Painted or Coated Specimens Subjected to Corrosive Environments

- ASTM D4752 – Standard Practice for Measuring MEK Resistance of Ethyl Silicate (Inorganic) Zinc-Rich Primers by Solvent Rub

- NFPA 90A – Standard for the Installation of Air-Conditioning and Ventilating Systems

1.04	Submittals

- See Section 01 30 00 – Administrative Requirements for submittal procedures.

- Product Data: Provide data indicating configuration, general assembly, and materials used in fabrication. Include catalog performance ratings that indicate airflow, and NC designation.

- Shop Drawings: Indicate configuration, general assembly, and materials used in fabrication.

- Project Record Documents:  Record actual locations of units and control components.

- Operation and Maintenance Data:  Include manufacturer's descriptive literature, operating instructions (if applicable), and maintenance and repair data.

- Warranty:  Submit manufacturer warranty and ensure forms have been completed in Owner's name and registered with manufacturer.

- Maintenance Materials:  Furnish the following for Owner's use in maintenance of project.

## 1.06	Quality Assurance

- Manufacturer Qualifications:  Company specializing in manufacturing the type of products specified in this section, with minimum ten years of documented experience.

## 1.07	Warranty

- See Section 01 7800 - Closeout Submittals, for additional warranty requirements.

- Provide 12 month manufacturer warranty from date of shipment of diffusers.

PART 2 – PRODUCTS

2.01	Manufacturer

- Basis of Design: Price Industries, Inc.

- Perforated Ceiling Diffusers Matching Return: Model PDDR

- Fire-Rated Perforated Ceiling Diffusers Matching Return, Flush Face: Model PDDR-FR

- Fire-Rated Perforated Ceiling Diffusers Matching Return, Extended Face: Model PDDRE-FR

- General:

  - The perforated face return diffuser shall be supplied to match supply air models in appearance and detail and provide ducted or non-ducted return airflow.

  - For plenum return, non-ducted applications, the return diffuser shall be provided with a special frame assembly to maximize free area.

  - The extended face return diffusers shall match the extended face supply diffusers for 15/16 inch tegular tile ceilings.

2.02	Perforated Face Ceiling Diffuser Matching Return

- Description:

  - Furnish and install Price model PDDR return diffusers in sizes and capacities as shown by the plans and air distribution schedule.

- Construction:

  - The return diffusers shall consist of a perforated air distribution face of no less than 51 percent free area, a heavy gauge steel back pan with [round] or [square] inlet collars as noted on the plans.

  - The perforated face screen construction shall be (select one):

    - [Steel]

    - [Aluminum]

  - The perforated face shall be removable from the diffuser face and shall be hinged for ease of removal of the face screen for cleaning purposes.

- Paint Specification:

  - Paint finish shall be (select one):

    - Baked-on powder coat finish.

      - The paint film thickness shall be a minimum of 2 mils.

      - The finish shall have a hardness of 2H as tested in accordance with ASTM D3363.

      - The finish shall pass an ASTM B117 Corrosive Environment Salt Spray Test for 1000 hours with no measurable creep, rusting or blistering as per ASTM D1654, D610 and D714.

      - The finish shall pass an ASTM D870 Water Immersion test of a minimum of 500 hours with no measurable with no rusting or blistering as per ASTM D610 and D714.

      - The finish shall have an impact resistance of 100 inch-pounds in accordance with ASTM D2794.

    - All components shall have a custom finish in a color to match a customer supplied sample.

- Mounting Frame:

  - The diffuser mounting frame shall be suitable for lay-in or surface mount applications with the following frame style (select one):

    - Style 3 – 15/16 inch wide flat T-bar

    - Style 1 – Surface mount

    - Style 17B – 9/16 inch wide bolt slot style T-bar

    - Style 15 – 15/16 inch wide flat T-bar for installation with tegular ceiling tiles

    - Style 4 – concealed spline

    - Style 2 – Snap-in

- Options (select all that apply):

  - Beaded Extended Neck:

    - The diffuser shall be supplied with a beaded neck extended to a depth of 2-1/2 inches.

  - Insulated Back pan (T-bar mounting frame only):

    - AFI –The diffuser back pan shall be externally insulated with ½ inch fiberglass with foil/scrim vapor barrier which meets the requirements of UL 181 and NFPA 90A.

    - R6 – The diffuser back pan shall be externally insulated with a molded heavy duty foil/scrim vapor barrier with an R-value of six. The insulation shall meet the requirements of UL 181 and NFPA 90A. (24 x 24 inch size only)

  - Light Shield:

    - The diffuser shall be supplied with a light shield to reduce visibility in the ceiling plenum from the room side. (Available for 22 x 22 inch and 22 x10 inch inlet sizes only)

  - Damper:

    - The diffuser shall be supplied with a steel opposed blade volume control damper (VCS3).

2.03	Fire-Rated Perforated Ceiling Diffusers Matching Return, Flush Face

- Description:

  - Furnish and install Price model PDDR-FR return diffusers in sizes and capacities as shown by the plans and air distribution schedule.

  - Diffusers shall be Fire-Rated Assemblies listed in the UL, Underwriters Laboratories Fire Resistance Directory and in the ULC, Underwriters Laboratories of Canada Equipment and Materials Directory.

  - Diffusers shall meet UL time versus temperature test criteria and NFPA 90A requirements.

  - This design is intended for use in an exposed grid suspended ceiling (T-bar Lay-in) with up to a three-hour rating and must be installed in accordance with the installation instructions.

- Construction:

  - The return diffusers shall consist of a perforated air distribution face of no less than 51 percent free area, and a heavy gauge steel back pan with [round] or [square] inlet collars as noted on the plans.

  - The diffuser construction shall be steel.

  - The perforated face shall be removable from the diffuser face and shall be fitted with hinges for ease of removal of the face screen for cleaning purposes.

  - The diffuser shall incorporate a non-adjustable fire-rated ceiling radiation damper.

- Paint Specification:

  - Paint finish shall be (select one):

    - Baked-on powder coat finish.

      - The paint film thickness shall be a minimum of 2 mils.

      - The finish shall have a hardness of 2H as tested in accordance with ASTM D3363.

      - The finish shall pass an ASTM B117 Corrosive Environment Salt Spray Test for 1000 hours with no measurable creep, rusting or blistering as per ASTM D1654, D610 and D714.

      - The finish shall pass an ASTM D870 Water Immersion test of a minimum of 500 hours with no measurable with no rusting or blistering as per ASTM D610 and D714.

      - The finish shall have an impact resistance of 100 inch-pounds in accordance with ASTM D2794.

    - All components shall have a custom finish in a color to match a customer supplied sample.

- Damper:

  - The diffuser shall be supplied with a galvanized steel, non-adjustable, fire-rated ceiling radiation damper.

- Thermal Blanket:

  - The diffuser shall be externally wrapped with a non-asbestos thermal blanket.

- Options (select all that apply):

  - Volume Control:

- The diffuser shall be supplied with a steel volume control damper that is room side adjustable for balancing.

  - Fusible Link:

- The diffuser shall be supplied with a fusible link rated for (select one):

      - 165 degrees Fahrenheit.

      - 212 degrees Fahrenheit.

2.04	Fire-Rated Perforated Ceiling Diffusers Matching Return, Extended Face

- Description:

  - Furnish and install Price model PDDRE-FR return diffusers in sizes and capacities as shown by the plans and air distribution schedule.

  - Diffusers shall be Fire-Rated Assemblies listed in the UL, Underwriters Laboratories Fire Resistance Directory and in the ULC, Underwriters Laboratories of Canada Equipment and Materials Directory.

  - Diffusers shall meet UL time versus temperature test criteria and NFPA 90A requirements.

  - This design is intended for use in an exposed grid suspended ceiling (T-bar Lay-in) with up to a three-hour rating and must be installed in accordance with the installation instructions.

- Construction:

  - The return diffusers shall consist of a perforated air distribution face of no less than 51 percent free area that extends 3/8 inch below the ceiling plane, and a heavy gauge steel back pan with [round] or [square] inlet collars as noted on the plans.

  - The diffuser construction shall be steel.

  - The perforated face shall be removable from the diffuser face and shall be fitted with hinges for ease of removal of the face screen for cleaning purposes.

  - The diffuser shall incorporate a non-adjustable fire-rated ceiling radiation damper.

- Paint Specification:

  - Paint finish shall be (select one):

    - Baked-on powder coat finish.

      - The paint film thickness shall be a minimum of 2 mils.

      - The finish shall have a hardness of 2H as tested in accordance with ASTM D3363.

      - The finish shall pass an ASTM B117 Corrosive Environment Salt Spray Test for 1000 hours with no measurable creep, rusting or blistering as per ASTM D1654, D610 and D714.

      - The finish shall pass an ASTM D870 Water Immersion test of a minimum of 500 hours with no measurable with no rusting or blistering as per ASTM D610 and D714.

      - The finish shall have an impact resistance of 100 inch-pounds in accordance with ASTM D2794.

    - All components shall have a custom finish in a color to match a customer supplied sample.

- Damper:

  - The diffuser shall be supplied with a galvanized steel, non-adjustable, fire-rated ceiling radiation damper.

- Thermal Blanket:

  - The diffuser shall be externally wrapped with a non-asbestos thermal blanket.

- Options (select all that apply):

  - Volume Control:

- The diffuser shall be supplied with a steel volume control damper that is room side adjustable for balancing.

  - Fusible Link:

- The diffuser shall be supplied with a fusible link rated for (select one):

- 165 degrees Fahrenheit.

- 212 degrees Fahrenheit.

PART 3 – EXECUTION

3.01	Examination

- Verify that conditions are suitable for installation.

- Verify that field measurements are as shown on the drawings.

3.02 	Installation

- Install in accordance with manufacturer’s instructions.

- See drawings for the size(s) and locations of diffusers.

3.03 	Field Quality Control

- See Section 01 40 00 – Quality Requirements for additional requirements.

3.05 	Cleaning

- See Section 01 74 19 – Construction Waste Management and Disposal for additional requirements.

3.06 	Closeout Activities

- See Section 01 78 00 – Closeout Submittals for closeout documentation requirements.

- See Section 01 79 00 – Demonstration and Training for additional requirements.