Price Architectural Perforated Face Supply Diffuser

Division 23 – Heating, Ventilating, and Air Conditioning

Section 23 37 13 – Diffusers, Registers, and Grilles

The following specification is for a defined application. Price would be pleased to assist in developing a specification for your specific need.

PART 1 – GENERAL

  - Section includes:

- Perforated Supply

  - Related Requirements

- Section 01 30 00 – Administrative Requirements

- Section 01 40 00 – Quality Requirements

- Section 01 74 21 – Construction/Demolition Waste Management and Disposal

- Section 01 78 00  – Closeout Submittals

- Section 01 79 00 – Demonstration and Training

  - Reference Standards

- All referenced standards and recommended practices in this section pertain to the most recent publication thereof, including all addenda and errata.

- ASHRAE 55 – Standard for Thermal Environmental Conditions for Human Occupancy

- ASHRAE 70 – Standard Method of Testing the Performance of Air Outlets and Air Inlets

- ASTM D610 – Standard Practice for Evaluating Degree of Rusting on Painted Steel Surfaces

- ASTM D714 – Test Method for Evaluating Degree of Blistering of Paints

- ASTM D1308 – Standard Test Method for Effect of Household Chemicals on Clear and Pigmented Organic Finishes

- ASTM D1654 – Standard Test Method for Evaluation of Painted or Coated Specimens Subjected to Corrosive Environments

- ASTM D4752 – Standard Practice for Measuring MEK Resistance of Ethyl Silicate (Inorganic) Zinc-Rich Primers by Solvent Rub

- NFPA 90A – Standard for the Installation of Air-Conditioning and Ventilating Systems

1.04	Submittals

- See Section 01 30 00 – Administrative Requirements for submittal procedures.

- Product Data: Provide data indicating configuration, general assembly, and materials used in fabrication. Include catalog performance ratings that indicate airflow, and NC designation.

- Shop Drawings: Indicate configuration, general assembly, and materials used in fabrication.

- Project Record Documents:  Record actual locations of units and control components.

- Operation and Maintenance Data:  Include manufacturer's descriptive literature, operating instructions (if applicable), and maintenance and repair data.

- Warranty:  Submit manufacturer warranty and ensure forms have been completed in Owner's name and registered with manufacturer.

- Maintenance Materials:  Furnish the following for Owner's use in maintenance of project.

## 1.06	Quality Assurance

- Manufacturer Qualifications:  Company specializing in manufacturing the type of products specified in this section, with minimum ten years of documented experience.

## 1.07	Warranty

- See Section 01 78 00 - Closeout Submittals, for additional warranty requirements.

- Provide 12 month manufacturer warranty from date of shipment of diffusers.

PART 2 – PRODUCTS

2.01	Manufacturer

- Basis of Design: Price Industries, Inc.

- Architectural Perforated Face Supply Diffuser: Model PDS

- General:

  - The perforated face supply diffuser shall provide ducted supply airflow, and shall be supplied to match return air models in appearance and detail.

2.02	Perforated Ceiling Supply Diffuser

- Description:

  - Furnish and install Price model PDS supply diffusers in sizes and capacities as shown by the plans and air distribution schedule.

- Construction:

  - The diffuser shall include fully adjustable louvered pattern controllers mounted on the face panel. The pattern controllers shall permit four-way, three-way, two-way, two-way corner, or one-way airflow patterns.

  - The diffuser shall have a [square] or [round] neck as indicated on the drawing or diffuser schedule.

  - The backpan and perforated face shall be coated steel construction, with snap-in mounting to the extruded aluminum border and mounting frame. The framed face panel sub-assembly shall connect to the backpan with spring clip latches for ease of removal and access to pattern controllers.

  - When installed, the face panel shall be flush with the border frame.

- Performance:

  - Air deflector modules shall allow full field adjustment of airflow pattern from one-way to four-way discharge without affecting the free area or the pressure and noise performance of the diffuser.

- Paint Specification:

  - Paint finish shall be (select one):

    - Baked-on powder coat finish.

      - The paint film thickness shall be a minimum of 2 mils.

      - The finish shall have a hardness of 2H as tested in accordance with ASTM D3363.

      - The finish shall pass an ASTM B117 Corrosive Environment Salt Spray Test for 1000 hours with no measurable creep, rusting or blistering as per ASTM D1654, D610 and D714.

      - The finish shall pass an ASTM D870 Water Immersion test of a minimum of 500 hours with no measurable with no rusting or blistering as per ASTM D610 and D714.

      - The finish shall have an impact resistance of 100 inch-pounds in accordance with ASTM D2794.

    - All components shall have a custom finish in a color to match a customer supplied sample.

- Mounting Frame:

  - The diffuser mounting frame shall be suitable for lay-in or surface mount applications with the following frame style (select one):

    - Surface mount

- Magnetic Resonance Imaging (MRI) Construction:

  - The diffuser shall be supplied with an all-aluminum construction for MRI applications.

  - The MRI option does not include a volume control damper.

PART 3 – EXECUTION

3.01	Examination

- Verify that conditions are suitable for installation.

- Verify that field measurements are as shown on the drawings.

3.02 	Installation

- Install in accordance with manufacturer’s instructions.

- See drawings for the size(s) and locations of diffusers.

3.03 	Field Quality Control

- See Section 01 40 00 – Quality Requirements for additional requirements.

3.05 	Cleaning

- See Section 01 74 19 – Construction Waste Management and Disposal for additional requirements.

3.06 	Closeout Activities

- See Section 01 78 00 – Closeout Submittals for closeout documentation requirements.

- See Section 01 79 00 – Demonstration and Training for additional requirements.