Price Industrial Grille

Division 23 – Heating, Ventilating, and Air Conditioning

Section 23 37 13 – Diffusers, Registers, and Grilles

The following specification is for a defined application. Price would be pleased to assist in developing a specification for your specific need.

PART 1 – GENERAL

  - Section includes:

- Industrial Grille.

  - Related Requirements

- Section 01 30 00 – Administrative Requirements

- Section 01 40 00 – Quality Requirements

- Section 01 60 00 – Product Requirements

- Section 01 74 21 – Construction/Demolition Waste Management and Disposal

- Section 01 78 00  – Closeout Submittals

- Section 01 79 00 – Demonstration and Training

  - Reference Standards

- All referenced standards and recommended practices in this section pertain to the most recent publication thereof, including all addenda and errata.

- ASHRAE 55 – Thermal Environmental Conditions for Human Occupancy.

- ASHRAE 70 – Method of Testing the Performance of Air Outlets and Air Inlets.

- ASTM D610 – Standard Practice for Evaluating Degree of Rusting on Painted Steel Surfaces.

- ASTM D714 – Standard Test Method for Evaluating Degree of Blistering of Paints.

- ASTM D1308 – Standard Test Method for Effect of Household Chemicals on Clear and Pigmented Organic Finishes.

- ASTM D4752 – Standard Practice for Measuring MEK Resistance of Ethyl Silicate (Inorganic) Zinc-Rich Primers by Solvent Rub.

- NFPA 90A – Standard for the Installation of Air-Conditioning and Ventilating Systems.

1.04	Submittals

- See Section 01 30 00 – Administrative Requirements for submittal procedures.

- Product Data: Provide data indicating configuration, general assembly, and materials used in fabrication. Include catalog performance ratings that indicate airflow, and NC designation.

- Shop Drawings: Indicate configuration, general assembly, and materials used in fabrication.

- Project Record Documents:  Record actual locations of units and control components.

- Operation and Maintenance Data:  Include manufacturer's descriptive literature, operating instructions (if applicable), and maintenance and repair data.

- Warranty:  Submit manufacturer warranty and ensure forms have been completed in Owner's name and registered with manufacturer.

- Maintenance Materials:  Furnish the following for Owner's use in maintenance of project.

## 1.06	Quality Assurance

- Manufacturer Qualifications:  Company specializing in manufacturing the type of products specified in this section, with minimum ten years of documented experience.

  - Warranty

- See Section 01 78 00 - Closeout Submittals, for additional warranty requirements.

- Provide 12 month manufacturer warranty from date of shipment of grilles and registers.

PART 2 – PRODUCTS

2.01	Industrial Grilles

- Basis of Design: Price Industries, Inc.

- Industrial Grille, 1.5 inch spacing: Model 151, 152, 152G

- Industrial Grille, 3.0 inch spacing: Model 301, 301G, 302, 302G

- Modular Industrial Grille, 1.5 inch spacing: Model MIG

2.02	Industrial Grilles, 1.5 Inch Spacing

- Description:

  - Furnish and install Price Model [151], [152], [152G] industrial supply grilles of sizes and mounting types indicated on the plans and air distribution schedule.

- Construction:

  - The grilles shall be [single deflection (Model 151)] or [double deflection (Models 152 and 152G)] type with [one set] or [two sets] of fully adjustable 1-1/4 inch deep streamlined deflection blades spaced 1-1/2 inches on center. The front blades shall run parallel to the [long] or [short] dimension of the grille, as indicated on the outlet schedule.

  - The grille blades, border, and mullions material shall be heavy extruded aluminum construction.

  - The individually adjustable blades shall index and lock into position at 0, 15, 30, and 45 degrees deflection in either direction. The grille indexing device shall be stainless steel construction.

- Paint Specification:

  - Paint finish shall be (select one):

    - Baked-on powder coat finish.

      - The paint film thickness shall be a minimum of 2 mils.

      - The finish shall have a hardness of 2H as tested in accordance with ASTM D3363.

      - The finish shall pass an ASTM B117 Corrosive Environment Salt Spray Test for 1000 hours with no measurable creep, rusting or blistering as per ASTM D1654, D610 and D714.

      - The finish shall pass an ASTM D870 Water Immersion test of a minimum of 500 hours with no measurable with no rusting or blistering as per ASTM D610 and D714.

      - The finish shall have an impact resistance of 100 inch-pounds in accordance with ASTM D2794.

    - All components shall have a custom finish in a color to match a customer supplied sample.

- Options:

  - Gang-operated Blades:

    - The [front] or [rear] blades shall be linked and gang operable from a face mounted pole operator. The blades, frame, pole operator, and movement bar shall be extruded aluminum construction.

  - Opposed Blade Damper:

    - The grille shall be supplied with [a coated steel (D)] or [an aluminum with mill finish (DAL)] opposed blade damper.

    - The damper shall be operable from the grille face.

    - [Optional]: The damper shall be coated heavy duty 18 gauge cold rolled steel construction, and shall come fitted with a face accessible screw type blade locking mechanism.

  - Border Style:

    - The grille shall be suitable for sidewall mounting, complete with a border in the following style (select one):

      - Surface Mount with 1-1/4 inch flat border.

      - Trunk Latch border (not available for model 152G).

      - Inverted frame, no latch.

  - Mounting Frames:

    - The grille shall be supplied with a 3/8 inch flat border mounting frame.

  - Fastening:

    - The grille shall be supplied with the following fastening method (select one):

      - Countersunk screw holes with factory-supplied screws.

      - No screw holes.

2.03	Industrial Grilles, 3 Inch Spacing

- Description:

  - Furnish and install Price Model [301], [301G], [302], [302G] industrial supply grilles of sizes and mounting types indicated on the plans and air distribution schedule.

- Construction:

  - The grilles shall be [single deflection (Models 301 and 301G)] or [double deflection (Models 302 and 302G)] type with [one set] or [two sets] of fully adjustable 3 inch deep streamlined deflection blades spaced 3 inches on center. The front blades shall run parallel to the [long] or [short] dimension of the grille, as indicated on the outlet schedule.

  - The grille blades and mullions shall be heavy extruded aluminum construction. The border shall be heavy gauge steel construction.

- Paint Specification:

  - Paint finish shall be (select one):

    - Baked-on powder coat finish.

      - The paint film thickness shall be a minimum of 2 mils.

      - The finish shall have a hardness of 2H as tested in accordance with ASTM D3363.

      - The finish shall pass an ASTM B117 Corrosive Environment Salt Spray Test for 1000 hours with no measurable creep, rusting or blistering as per ASTM D1654, D610 and D714.

      - The finish shall pass an ASTM D870 Water Immersion test of a minimum of 500 hours with no measurable with no rusting or blistering as per ASTM D610 and D714.

      - The finish shall have an impact resistance of 100 inch-pounds in accordance with ASTM D2794.

    - All components shall have a custom finish in a color to match a customer supplied sample.

- Options:

  - Gang-operated Blades:

    - The [front] or [rear] blades shall be linked and gang operable from a face mounted pole operator. The blades, frame, pole operator, and movement bar shall be extruded aluminum construction.

  - Opposed Blade Damper:

    - The grille shall be supplied with [a coated steel (D)] or [an aluminum with mill finish (DAL)] opposed blade damper.

    - The damper shall be operable from the grille face.

    - [Optional]: The damper shall be coated heavy-duty 18 gauge cold rolled steel construction, and shall com fitted with a face accessible screw type blade locking mechanism.

  - Border Style:

    - The grille shall be suitable for sidewall mounting, complete with a surface mount with a 1-1/4 inch flat border border.

  - Mounting Frames:

    - The grille shall be supplied with a 3/8 inch flat border mounting frame.

  - Fastening:

    - The grille shall be supplied with the following fastening method (select one):

      - Countersunk screw holes with factory-supplied screws.

      - No screw holes.

2.04	Modular Industrial Grilles

- Description:

  - Furnish and install Price Model MIG modular industrial grilles of sizes and mounting types indicated on the plans and air distribution schedule.

- Construction:

  - The grilles shall consist of [single] or [multiple] square grilles mounted to a heavy gauge steel panel with quick-release fasteners.

  - The grilles shall be double deflection type with two sets of fully adjustable 1-1/4 inch deep streamlined deflection blades spaced 1.5 inches on center. The blades shall run parallel to the [long] or [short] dimension of the grille, as indicated on the outlet schedule.

  - The individually adjustable blades shall index and lock into position at 0, 15, 30, and 45 degrees deflection.

  - The grille blades and frame shall be heavy extruded aluminum construction. The grille indexing device shall be stainless steel construction.

- Paint Specification:

  - Paint finish shall be (select one):

    - Baked-on powder coat finish.

      - The paint film thickness shall be a minimum of 2 mils.

      - The finish shall have a hardness of 2H as tested in accordance with ASTM D3363.

      - The finish shall pass an ASTM B117 Corrosive Environment Salt Spray Test for 1000 hours with no measurable creep, rusting or blistering as per ASTM D1654, D610 and D714.

      - The finish shall pass an ASTM D870 Water Immersion test of a minimum of 500 hours with no measurable with no rusting or blistering as per ASTM D610 and D714.

      - The finish shall have an impact resistance of 100 inch-pounds in accordance with ASTM D2794.

    - All components shall have a custom finish in a color to match a customer supplied sample.

- Options:

  - Fastening:

    - The grille shall be supplied with the following fastening method (select one):

      - Countersunk screw holes with factory-supplied screws.

      - No screw holes.

PART 3 – EXECUTION

3.01	Examination

- Verify that conditions are suitable for installation.

- Verify that field measurements are as shown on the drawings.

3.02 	Installation

- Install in accordance with manufacturer’s instructions.

- See drawings for the size(s) and locations of grilles and registers.

3.03 	Field Quality Control

- See Section 01 40 00 – Quality Requirements for additional requirements.

3.05 	Cleaning

- See Section 01 74 19 – Construction Waste Management and Disposal for additional requirements.

3.06 	Closeout Activities

- See Section 01 78 00 – Closeout Submittals for closeout documentation requirements.

- See Section 01 79 00 – Demonstration and Training for additional requirements.