Price Airfoil Supply Grille

Division 23 – Heating, Ventilating, and Air Conditioning

Section 23 37 13 – Diffusers, Registers, and Grilles

The following specification is for a defined application. Price would be pleased to assist in developing a specification for your specific need.

PART 1 – GENERAL

  - Section includes:

- Airfoil Supply Grille.

  - Related Requirements

- Section 01 30 00 – Administrative Requirements

- Section 01 40 00 – Quality Requirements

- Section 01 60 00 – Product Requirements

- Section 01 74 21 – Construction/Demolition Waste Management and Disposal

- Section 01 78 00  – Closeout Submittals

- Section 01 79 00 – Demonstration and Training

  - Reference Standards

- All referenced standards and recommended practices in this section pertain to the most recent publication thereof, including all addenda and errata.

- ASHRAE Standard 55 – Thermal Environmental Conditions for Human Occupancy.

- ASHRAE Standard 70 – Method of Testing the Performance of Air Outlets and Air Inlets.

- ASTM D610 – Standard Practice for Evaluating Degree of Rusting on Painted Steel Surfaces.

- ASTM D714 – Standard Test Method for Evaluating Degree of Blistering of Paints.

- ASTM D1308 – Standard Test Method for Effect of Household Chemicals on Clear and Pigmented Organic Finishes.

- ASTM D4752 – Standard Practice for Measuring MEK Resistance of Ethyl Silicate (Inorganic) Zinc-Rich Primers by Solvent Rub.

- NFPA Standard 90A – Standard for the Installation of Air-Conditioning and Ventilating Systems.

1.04	Submittals

- See Section 01 30 00 – Administrative Requirements for submittal procedures.

- Product Data: Provide data indicating configuration, general assembly, and materials used in fabrication. Include catalog performance ratings that indicate air flow, and NC designation.

- Shop Drawings: Indicate configuration, general assembly, and materials used in fabrication.

- Project Record Documents:  Record actual locations of units and control components.

- Operation and Maintenance Data:  Include manufacturer's descriptive literature, operating instructions (if applicable), and maintenance and repair data.

- Warranty:  Submit manufacturer warranty and ensure forms have been completed in Owner's name and registered with manufacturer.

- Maintenance Materials:  Furnish the following for Owner's use in maintenance of project.

## 1.06	Quality Assurance

- Manufacturer Qualifications:  Company specializing in manufacturing the type of products specified in this section, with minimum ten years of documented experience.

## 1.07	Warranty

- See Section 01 7800 - Closeout Submittals, for additional warranty requirements.

- Provide 12 month manufacturer warranty from date of shipment of grilles and registers.

PART 2 – PRODUCTS

2.01	Airfoil Supply Grilles

- Basis of Design: Price Industries, Inc.

- Airfoil Supply Grille, Single Deflection: Model 21, 31, 21D, 21DAL, 31D, 31DAL

- Airfoil Supply Grille, Double Deflection: Model 22, 32, 22D, 22DAL, 32D, 32DAL

- General:

  - The airfoil supply grille shall be supplied with extruded aluminum blades and border with individually adjustable airfoil blades for non-turbulent airflow.

2.02	 Airfoil Supply Grilles – Single Deflection

- Description:

  - Furnish and install Price Model [21], [31], [21D], [21DAL], [31D], [31DAL] single deflection airfoil supply grilles and registers of sizes and mounting types designated by the plans and air distribution schedule.

- Construction:

  - The grille material shall be aluminum.

  - The grille shall have precision mitered corners.

  - The adjustable airfoil blades shall be secured in place by a stainless steel tensioning wire.

  - The grilles front blade orientation shall be (select one):

    - Parallel to the long dimension.

    - Parallel to the short dimension.

  - The single deflection cores shall have (select one):

    - One set of blades with ¾ inch on center blade spacing (Model 21)

    - One set of blades with ½ inch on center blade spacing (Model 31).

  - The minimum grille size shall be 6 x 4 inches. The maximum grille size shall be [36 inches x 96 inches] or [48 inches x 48 inches with steel frame option].

  - The grille shall be supplied with a mullion when nominal grille dimensions exceed 20 inches.

- Paint Specification:

  - Paint finish shall be (select one):

    - Baked-on powder coat finish.

      - The paint film thickness shall be a minimum of 2 mils.

      - The finish shall have a hardness of 2H as tested in accordance with ASTM D3363.

      - The finish shall pass an ASTM B117 Corrosive Environment Salt Spray Test for 1000 hours with no measurable creep, rusting or blistering as per ASTM D1654, D610 and D714.

      - The finish shall pass an ASTM D870 Water Immersion test of a minimum of 500 hours with no measurable with no rusting or blistering as per ASTM D610 and D714.

      - The finish shall have an impact resistance of 100 inch-pounds in accordance with ASTM D2794.

    - All components shall have a custom finish in a color to match a customer supplied sample.

- Options:

  - Opposed Blade Damper:

    - The grille shall be supplied with [a coated steel (D)] or [an aluminum with mill finish (DAL)] opposed blade damper.

  - Border Style:

    - The grille shall be suitable for sidewall mounting or T-bar lay-in mounting, complete with a border in the following style (select one):

      - Surface Mount with 1-1/4 inch curved border.

      - Surface Mount with 1-1/4 inch flat border.

      - Surface Mount with 1 inch narrow border.

      - Exposed duct with 13/16 border.

      - T-bar Mount 1-1/4 inch steel flat border.

  - Mounting Frames:

    - The grille shall be supplied with a 3/8 inch flat border mounting frame.

  - Fastening:

    - The grille shall be supplied with the following fastening method (select one):

      - Countersunk screw holes with factory-supplied screws.

      - Concealed fastening.

      - No screw holes.

2.03	Airfoil Supply Grilles – Double Deflection

- Description:

  - Furnish and install Price Model [22], [32], [22D], [22DAL], [32D], [32DAL] double deflection airfoil supply grilles and registers of sizes and mounting types designated by the plans and air distribution schedule.

- Construction:

  - Grille material shall be aluminum.

  - The grille shall have precision mitered corners.

  - The adjustable airfoil blades shall be secured in place by a stainless steel tensioning wire.

  - The grilles front blade orientation shall be (select one):

    - Parallel to the long dimension.

    - Parallel to the short dimension.

  - The double deflection cores shall have (select one):

    - Both sets of blades with ¾ inch on center blade spacing (Model 22)

    - The front blades with ½ inch on center blade spacing and the rear blades ¾ inch on center spacing (Model 32).

  - The minimum grille size shall be 6 x 4 inches. The maximum grille size shall be [36 inches x 96 inches] or [48 inches x 48 inches with steel frame option].

  - The grille shall be supplied with a mullion when nominal grille dimensions exceed 20 inches.

- Paint Specification:

  - Paint finish shall be (select one):

    - Baked-on powder coat finish.

      - The paint film thickness shall be a minimum of 2 mils.

      - The finish shall have a hardness of 2H as tested in accordance with ASTM D3363.

      - The finish shall pass an ASTM B117 Corrosive Environment Salt Spray Test for 1000 hours with no measurable creep, rusting or blistering as per ASTM D1654, D610 and D714.

      - The finish shall pass an ASTM D870 Water Immersion test of a minimum of 500 hours with no measurable with no rusting or blistering as per ASTM D610 and D714.

      - The finish shall have an impact resistance of 100 inch-pounds in accordance with ASTM D2794.

    - All components shall have a custom finish in a color to match a customer supplied sample.

- Options:

    - Opposed Blade Damper:

        - The register shall be supplied with [a coated steel (D)] or [aluminum with mill finish (DAL)] opposed blade damper.

    - Border Style:

        - The grille shall be suitable for sidewall mounting or exposed duct mounting, complete with a border in the following style (select one):

      - Surface Mount with 1-1/4 inch curved border.

      - Surface Mount with 1-1/4 inch flat border.

      - Surface Mount with 1 inch narrow border.

      - Exposed duct with 13/16 border.

      - T-bar Mount 1-1/4 inch steel flat border.

    - Mounting Frames:

      - The grille shall be supplied with a 3/8 inch flat border mounting frame.

    - Fastening:

      - The grille shall be supplied with the following fastening method (select one):

        - Countersunk screw holes complete with oval-head screws.

        - Concealed fastening.

        - No screw holes.

PART 3 – EXECUTION

3.01	Examination

- Verify that conditions are suitable for installation.

- Verify that field measurements are as shown on the drawings.

3.02 	Installation

- Install in accordance with manufacturer’s instructions.

- See drawings for the size(s) and locations of grilles and registers.

3.03 	Field Quality Control

- See Section 01 40 00 – Quality Requirements for additional requirements.

3.05 	Cleaning

- See Section 01 74 19 – Construction Waste Management and Disposal for additional requirements.

3.06 	Closeout Activities

- See Section 01 78 00 – Closeout Submittals for closeout documentation requirements.

- See Section 01 79 00 – Demonstration and Training for additional requirements.