Price Aluminum Louvered Grille

Division 23 – Heating, Ventilating, and Air Conditioning

Section 23 37 13 – Diffusers, Registers, and Grilles

The following specification is for a defined application. Price would be pleased to assist in developing a specification for your specific need.

PART 1 – GENERAL

  - Section includes:

- Aluminum Louvered Grille.

  - Related Requirements

- Section 01 30 00 – Administrative Requirements

- Section 01 40 00 – Quality Requirements

- Section 01 60 00 – Product Requirements

- Section 01 74 21 – Construction/Demolition Waste Management and Disposal

- Section 01 78 00  – Closeout Submittals

- Section 01 79 00 – Demonstration and Training

  - Reference Standards

- All referenced standards and recommended practices in this section pertain to the most recent publication thereof, including all addenda and errata.

- ASTM 610 – Standard Practice for Evaluating Degree of Rusting on Painted Steel Surfaces

- ASTM 714 – Test Method for Evaluating Degree of Blistering of Paints

- ASTM D1308 – Standard Test Method for Effect of Household Chemicals on Clear and Pigmented Organic Finishes

- ASTM D1654 – Standard Test Method for Evaluation of Painted or Coated Specimens Subjected to Corrosive Environments

- ASTM D4752 – Standard Practice for Measuring MEK Resistance of Ethyl Silicate (Inorganic) Zinc-Rich Primers by Solvent Rub

1.04	Submittals

- See Section 01 30 00 – Administrative Requirements for submittal procedures.

- Product Data: Provide data indicating configuration, general assembly, and materials used in fabrication. Include catalog performance ratings that indicate airflow, and NC designation.

- Shop Drawings: Indicate configuration, general assembly, and materials used in fabrication.

- Project Record Documents:  Record actual locations of units and control components.

- Operation and Maintenance Data:  Include manufacturer's descriptive literature, operating instructions (if applicable), and maintenance and repair data.

- Warranty:  Submit manufacturer warranty and ensure forms have been completed in Owner's name and registered with manufacturer.

- Maintenance Materials:  Furnish the following for Owner's use in maintenance of project.

## 1.06	Quality Assurance

- Manufacturer Qualifications:  Company specializing in manufacturing the type of products specified in this section, with minimum ten years of documented experience.

## 1.07	Warranty

- See Section 01 7800 - Closeout Submittals, for additional warranty requirements.

- Provide 12 month manufacturer warranty from date of shipment of grilles and registers.

PART 2 – PRODUCTS

2.01	Steel Louvered Grille

- Basis of Design: Price Industries, Inc.

- Aluminum Louvered Supply Grille: Model 610, 620

- Aluminum Louvered Return Grille: Model 630, 635, 610Z

2.02	Aluminum Louvered Supply Grille

- Description:

  - Furnish and install Price Model [610], [620] aluminum louvered supply grilles and registers of sizes and mounting types designated by the plans and air distribution schedule.

- Construction:

  - Grilles shall be [single deflection] or [double deflection] louver type, and shall have (select one):

    - One set of fully adjustable blades, with 3/4 inch on center blade spacing (Model 610).

    - Two sets of fully adjustable blades, with the second set behind the first set, and with 3/4 inch on center blade spacing (Model 620).

  - The grilles front blade orientation shall be (select one), as indicated on the outlet schedule.

    - Front blades parallel to the long dimension.

    - Front blades parallel to the short dimension.

  - The blades and border shall be aluminum construction.

  - The minimum grille size shall be six inches by four inches. The maximum one-piece grille size shall be 48 inches x 48 inches.

- Paint Specification:

  - Paint finish shall be (select one):

    - Baked-on powder coat finish.

      - The paint film thickness shall be a minimum of 2 mils.

      - The finish shall have a hardness of 2H as tested in accordance with ASTM D3363.

      - The finish shall pass an ASTM B117 Corrosive Environment Salt Spray Test for 1000 hours with no measurable creep, rusting or blistering as per ASTM D1654, D610 and D714.

      - The finish shall pass an ASTM D870 Water Immersion test of a minimum of 500 hours with no measurable with no rusting or blistering as per ASTM D610 and D714.

      - The finish shall have an impact resistance of 100 inch-pounds in accordance with ASTM D2794.

    - All components shall have a custom finish in a color to match a customer supplied sample.

- Options:

  - Opposed Blade Damper:

    - The grille shall be supplied with a [coated aluminum (DAL)] or [galvanized steel (D)] opposed blade damper.

  - Border Style:

    - The grille shall be suitable for [sidewall mounting] or [T-bar lay-in mounting], complete with a border in the following style (select one):

      - 1-1/4 inch flat border.

      - 1 inch narrow border.

      - Panel mount border for T-bar installation. The maximum grille size shall equal the module size minus four inches. The panel module shall be the following size (select one):

        - 12 x 12 inches.

        - 24 x 12 inches.

        - 24 x 24 inches.

        - 48 x 24 inches.

  - Mounting Frames:

    - The grille shall be supplied with (select one):

      - 3/8 inch flat border mounting frame.

      - spiral duct mounting frame.

  - Fastening:

    - The grille shall be supplied with the following fastening method (select one):

      - Countersunk screw holes complete with Philips-head screws.

      - No screw holes (default for T-bar installation).

  - Insect Screen:

    - The grille shall be supplied with an 18 x16 aluminum mesh insect screen. [Not available with opposed blade damper.]

2.03	Aluminum Louvered Return Grille

- Description:

  - Furnish and install Price Model [630], [635], [610Z] aluminum louvered return grilles and registers of sizes and mounting types designated by the plans and air distribution schedule.

- Construction:

  - Grilles shall be 45 degree deflection fixed louver type, and shall have (select one):

      - One set of blades with 3/4 inch on center blade spacing [Model 630]

      - One set of blades with 1/2 inch on center blade spacing [Model 635]

      - One set of fixed blades with 0 degree deflection and 3/4 inch on center blade spacing [Model 610Z].

  - The grilles front blade orientation shall be (select one), as indicated on the outlet schedule.

    - Front blades parallel to the long dimension.

    - Front blades parallel to the short dimension.

  - The blades and border shall be extruded aluminum construction.

  - The minimum grille size shall be six inches by four inches. The maximum one-piece grille size shall be [36 inches x 96 inches] or [48 inches x 48 inches with steel frame option].

- Paint Specification:

  - Paint finish shall be (select one):

    - Baked-on powder coat finish.

      - The paint film thickness shall be a minimum of 2 mils.

      - The finish shall have a hardness of 2H as tested in accordance with ASTM D3363.

      - The finish shall pass an ASTM B117 Corrosive Environment Salt Spray Test for 1000 hours with no measurable creep, rusting or blistering as per ASTM D1654, D610 and D714.

      - The finish shall pass an ASTM D870 Water Immersion test of a minimum of 500 hours with no measurable with no rusting or blistering as per ASTM D610 and D714.

      - The finish shall have an impact resistance of 100 inch-pounds in accordance with ASTM D2794.

    - All components shall have a custom finish in a color to match a customer supplied sample.

- Options:

  - Opposed Blade Damper:

    - The register shall be supplied with a [coated aluminum (DAL)] or [galvanized steel (D)] opposed blade damper. The damper shall be operable from the register face.

  - Border Style:

    - The grille shall be suitable for [surface mounting], [T-bar lay-in mounting], [panel mounting], or [spiral duct frame mount], complete with a border in the following style (select one):

      - Surface Mount with 1-1/4 inch flat border.

      - Surface Mount with 1 inch narrow border.

      - Panel mount border for T-bar installation. The maximum grille size shall equal the module size minus four inches. The panel module shall be the following size (select one):

        - 12 x 12 inches.

        - 24 x 12 inches.

        - 24 x 24 inches.

        - 48 x 24 inches.

  - Mounting Frames:

    - The grille shall be supplied with (select one):

      - A 3/8 inch flat border mounting frame.

      - A 5/8 inch narrow border mounting frame.

  - Fastening:

    - The grille shall be supplied with the following fastening method (select one):

    - Countersunk screw holes complete with screws.

    - Concealed bracket (applies to Model 630 and surface mount only)

    - No screw holes. (default for T-bar frames)

  - Insect Screen:

    - The grille shall be supplied with an 18 x16 aluminum mesh insect screen.

  - Thin Line Return Dissipater (Nominal 22 x 22 inch size and Flat Face Border T-bar frame only):

    - The grille shall be supplied with a Thin Line Return Dissipater (TLRD) to provide sound power insertion loss across the full range of frequencies, and shall be suitable for ceiling and wall applications.

    - The manufacturer shall provide catalogued performance for insertion loss and transmission loss.

    - The TLRD shall be a high-quality welded galvanized steel construction. Satin Coat paint shall be available as an option.

    - The TLRD shall be factory-mounted to the grille and shipped as a one-piece construction to simplify field installation.

  - Light Shield:

    - The grille shall be supplied with a light shield to minimize the direct line of sight through the grille into the ceiling plenum and block reflected light from ceiling fixtures.

  - Magnetic Resonance Imaging (MRI) Construction:

    - The grille shall be supplied with an all-aluminum construction for MRI applications.

    - The grille module shall be 24 x 24 inches with a [T-bar] or [Narrow member] frame style.

    - The MRI option shall not include a volume control damper.

PART 3 – EXECUTION

3.01	Examination

- Verify that conditions are suitable for installation.

- Verify that field measurements are as shown on the drawings.

3.02 	Installation

- Install in accordance with manufacturer’s instructions.

- See drawings for the size(s) and locations of grilles and registers.

3.03 	Field Quality Control

- See Section 01 40 00 – Quality Requirements for additional requirements.

3.05 	Cleaning

- See Section 01 74 19 – Construction Waste Management and Disposal for additional requirements.

3.06 	Closeout Activities

- See Section 01 78 00 – Closeout Submittals for closeout documentation requirements.

- See Section 01 79 00 – Demonstration and Training for additional requirements.