Price Airfoil Return Grille

Division 23 – Heating, Ventilating, and Air Conditioning

Section 23 37 13 – Diffusers, Registers, and Grilles

The following specification is for a defined application. Price would be pleased to assist in developing a specification for your specific need.

PART 1 – GENERAL

  - Section includes:

- Airfoil Return Grille.

  - Related Requirements

- Section 01 30 00 – Administrative Requirements

- Section 01 40 00 – Quality Requirements

- Section 01 60 00 – Product Requirements

- Section 01 74 21 – Construction/Demolition Waste Management and Disposal

- Section 01 78 00  – Closeout Submittals

- Section 01 79 00 – Demonstration and Training

  - Reference Standards

- All referenced standards and recommended practices in this section pertain to the most recent publication thereof, including all addenda and errata.

- ASHRAE Standard 70 – Method of Testing the Performance of Air Outlets and Air Inlets

- ASTM 610 – Standard Practice for Evaluating Degree of Rusting on Painted Steel Surfaces

- ASTM 714 – Test Method for Evaluating Degree of Blistering of Paints

- ASTM D1308 – Standard Test Method for Effect of Household Chemicals on Clear and Pigmented Organic Finishes

- ASTM D1654 – Standard Test Method for Evaluation of Painted or Coated Specimens Subjected to Corrosive Environments

- ASTM D4752 – Standard Practice for Measuring MEK Resistance of Ethyl Silicate (Inorganic) Zinc-Rich Primers by Solvent Rub

1.04	Submittals

- See Section 01 30 00 – Administrative Requirements for submittal procedures.

- Product Data: Provide data indicating configuration, general assembly, and materials used in fabrication. Include catalog performance ratings that indicate airflow, and NC designation.

- Shop Drawings: Indicate configuration, general assembly, and materials used in fabrication.

- Project Record Documents:  Record actual locations of units and control components.

- Operation and Maintenance Data:  Include manufacturer's descriptive literature, operating instructions (if applicable), and maintenance and repair data.

- Warranty:  Submit manufacturer warranty and ensure forms have been completed in Owner's name and registered with manufacturer.

- Maintenance Materials:  Furnish the following for Owner's use in maintenance of project.

## 1.06	Quality Assurance

- Manufacturer Qualifications:  Company specializing in manufacturing the type of products specified in this section, with minimum ten years of documented experience.

## 1.07	Warranty

- See Section 01 7800 - Closeout Submittals, for additional warranty requirements.

- Provide 12 month manufacturer warranty from date of shipment of grilles and registers.

PART 2 – PRODUCTS

2.01	 Airfoil Return Grilles

- Basis of Design: Price Industries, Inc.

- Airfoil Return Grille: Model 60, 60D, 60DAL, 70, 70D, 70DAL

- Airfoil Filter Return Grille: Model 60FH, 70FH

- General:

  - The airfoil Return grille shall be supplied with extruded aluminum blades and border with individually adjustable airfoil blades for non-turbulent airflow.

2.02	Airfoil Return Grilles

- Description:

  - Furnish and install Price Model [60], [60D], [60DAL], [70], [70D], [70DAL] airfoil return grilles and registers of sizes and mounting types designated by the plans and air distribution schedule.

- Construction:

  - Grilles shall be 45 degree deflection fixed louver type, and shall have (select one):

    - One set of blades with ¾ inch on center blade spacing (Model 60)

    - One set of blades with ½ inch on center blade spacing (Model 70).

  - The grilles front blade orientation shall be (select one), as indicated on the outlet schedule.

    - Front blades parallel to the long dimension.

    - Front blades parallel to the short dimension.

  - The blades and border shall be heavy duty extruded aluminum construction.

  - The minimum grille size shall be six inches by four inches. The maximum one-piece grille size shall be [36 inches x 96 inches] or [48 inches x 48 inches with steel frame option].

  - The grille shall be supplied with a mullion when nominal grille dimensions exceed 20 inches.

- Paint Specification:

  - Paint finish shall be (select one):

    - Baked-on powder coat finish.

      - The paint film thickness shall be a minimum of 2 mils.

      - The finish shall have a hardness of 2H as tested in accordance with ASTM D3363.

      - The finish shall pass an ASTM B117 Corrosive Environment Salt Spray Test for 1000 hours with no measurable creep, rusting or blistering as per ASTM D1654, D610 and D714.

      - The finish shall pass an ASTM D870 Water Immersion test of a minimum of 500 hours with no measurable with no rusting or blistering as per ASTM D610 and D714.

      - The finish shall have an impact resistance of 100 inch-pounds in accordance with ASTM D2794.

    - All components shall have a custom finish in a color to match a customer supplied sample.

- Options:

  - Opposed Blade Damper:

    - The grille shall be supplied with [a coated steel (D)] or [an aluminum with mill finish (DAL)] opposed blade damper.

  - Border Style:

    - The grille shall be suitable for sidewall mounting or T-bar lay-in mounting, complete with a border in the following style (select one):

      - Surface Mount with 1-1/4 inch curved border.

      - Surface Mount with 1-1/4 inch flat border.

      - Surface Mount with 1 inch narrow border.

      - Exposed duct with 15/16 border.

      - Panel mount border. The maximum grille size shall equal the module size minus four inches. The panel module shall be the following size (select one):

        - 12 x 12 inches.

        - 24 x 12 inches.

        - 24 x 24 inches.

        - 48 x 24 inches.

  - Mounting Frames:

    - The grille shall be supplied with a 3/8 inch flat border mounting frame.

  - Fastening:

    - The grille shall be supplied with the following fastening method (select one):

      - Countersunk screw holes complete with oval-head screws.

      - Concealed fastening.

      - Straight screw holes.

      - No screw holes.

2.03	Airfoil Filter Return Grilles

- Description:

  - Furnish and install Price Model [60FH], [70FH] airfoil filter return grilles and registers of sizes and mounting types designated by the plans and air distribution schedule.

- Construction:

  - Grilles shall have 45 degree deflection fixed louver type blades, and shall have (select one):

      - One set of blades with 3/4 inch on center blade spacing (Model 60)

      - One set of blades with 1/2 inch on center blade spacing (Model 70).

  - The grilles front blade orientation shall be (select one), as indicated on the outlet schedule.

    - Front blades parallel to the long dimension.

    - Front blades parallel to the short dimension.

  - The blades and border shall be heavy extruded aluminum construction.

  - The grille shall use a continuous length piano type hinge and quarter turn quick-release fasteners for filter access.

  - The filter frame shall accept one inch filter media.

  - The minimum grille size shall be six inches by four inches. The maximum one-piece grille size shall be [36 inches x 96 inches] or [48 inches x 48 inches with steel frame option].

  - The grille shall be supplied with a mullion when nominal grille dimensions exceed 20 inches.

- Paint Specification:

  - Paint finish shall be (select one):

    - Baked-on powder coat finish.

      - The paint film thickness shall be a minimum of 2 mils.

      - The finish shall have a hardness of 2H as tested in accordance with ASTM D3363.

      - The finish shall pass an ASTM B117 Corrosive Environment Salt Spray Test for 1000 hours with no measurable creep, rusting or blistering as per ASTM D1654, D610 and D714.

      - The finish shall pass an ASTM D870 Water Immersion test of a minimum of 500 hours with no measurable with no rusting or blistering as per ASTM D610 and D714.

      - The finish shall have an impact resistance of 100 inch-pounds in accordance with ASTM D2794.

    - All components shall have a custom finish in a color to match a customer supplied sample.

- Options:

  - Opposed Blade Damper:

    - The register shall be supplied with [a coated steel (D)] or [aluminum with mill finish (DAL)] opposed blade damper.

  - Border Style:

    - The grille shall be suitable for surface or T-bar mounting.

  - Mounting Frames:

    - The grille shall be supplied with a 3/8 inch flat border mounting frame.

  - Fastening:

    - The grille shall be supplied with the following fastening method (select one):

      - Countersunk screw holes complete with oval-head screws.

      - Concealed fastening.

      - Straight screw holes.

      - No screw holes.

PART 3 – EXECUTION

3.01	Examination

- Verify that conditions are suitable for installation.

- Verify that field measurements are as shown on the drawings.

3.02 	Installation

- Install in accordance with manufacturer’s instructions.

- See drawings for the size(s) and locations of grilles and registers.

3.03 	Field Quality Control

- See Section 01 40 00 – Quality Requirements for additional requirements.

3.05 	Cleaning

- See Section 01 74 19 – Construction Waste Management and Disposal for additional requirements.

3.06 	Closeout Activities

- See Section 01 78 00 – Closeout Submittals for closeout documentation requirements.

- See Section 01 79 00 – Demonstration and Training for additional requirements.