Price Concentric Ring Nozzle Diffusers

Division 23 – Heating, Ventilating, and Air Conditioning

Section 23 37 13 – Diffusers, Registers, and Grilles

The following specification is for a defined application. Price would be pleased to assist in developing a specification for your specific need.

PART 1 – GENERAL

  - Section includes:

- Concentric Ring Nozzle Diffusers

  - Related Requirements

- Section 01 30 00 – Administrative Requirements

- Section 01 40 00 – Quality Requirements

- Section 01 74 21 – Construction/Demolition Waste Management and Disposal

- Section 01 78 00  – Closeout Submittals

- Section 01 79 00 – Demonstration and Training

  - Reference Standards

- All referenced standards and recommended practices in this section pertain to the most recent publication thereof, including all addenda and errata.

- ASHRAE 70 – Method of Testing the Performance of Air Outlets and Air Inlets.

- ASTM 610 – Standard Practice for Evaluating Degree of Rusting on Painted Steel Surfaces.

- ASTM 714 – Test Method for Evaluating Degree of Blistering of Paints.

- ASTM D1308 – Standard Test Method for Effect of Household Chemicals on Clear and Pigmented Organic Finishes.

- ASTM D1654 – Standard Test Method for Evaluation of Painted or Coated Specimens Subjected to Corrosive Environments.

- ASTM D4752 – Standard Practice for Measuring MEK Resistance of Ethyl Silicate (Inorganic) Zinc-Rich Primers by Solvent Rub.

- UL 94 – Standard for Tests for Flammability of Plastic Materials for Parts in Devices and Appliances.

1.04	Submittals

- See Section 01 30 00 – Administrative Requirements for submittal procedures.

- Product Data: Provide data indicating configuration, general assembly, and materials used in fabrication. Include catalog performance ratings that indicate airflow, static pressure, and NC designation.

- Shop Drawings: Indicate configuration, general assembly, and materials used in fabrication.

- Certificates: Certify that air capacities, pressure drops, and selection procedures meet or exceed specified requirements.

- Project Record Documents:  Record actual locations of units and control components.

- Warranty:  Submit manufacturer warranty and ensure forms have been completed in Owner's name and registered with manufacturer.

- Maintenance Materials:  Furnish the following for Owner's use in maintenance of project.

## 1.06	Quality Assurance

- Manufacturer Qualifications:  Company specializing in manufacturing the type of products specified in this section, with minimum ten years of documented experience.

## 1.07	Warranty

- See Section 01 78 00 - Closeout Submittals, for additional warranty requirements.

- Provide 12 month manufacturer warranty from date of shipment of diffusers.

PART 2 – PRODUCTS

2.01	Manufacturer

- Basis of Design: Price Industries, Inc.

- Air Nozzle Diffusers: Model AND

- Air Nozzle Diffuser with Core: Model ANR

- Air Nozzle Diffuser without Core: Model ANF

2.02	Air Nozzle Diffusers

- Description:

  - Furnish and install Price model AND nozzle diffusers of sizes and mounting styles shown on the plans and air distribution schedule.

- Construction:

  - The air nozzle diffuser shall be 16 gauge cold rolled steel construction, with a series of concentric round nozzles.

  - The inner nozzle [assembly] or [assemblies] shall be manually adjustable to produce a swivel range of +/- 30 degrees within a fixed arc.

  - The nozzle diffuser shall be supplied (select one):

    - As a single diffuser.

    - With [two], [three], or [four] nozzles mounted within a common panel.

- Paint Specification:

  - Paint finish shall be (select one):

    - Baked-on powder coat finish.

      - The paint film thickness shall be a minimum of 2 mils.

      - The finish shall have a hardness of 2H as tested in accordance with ASTM D3363.

      - The finish shall pass an ASTM B117 Corrosive Environment Salt Spray Test for 1000 hours with no measurable creep, rusting or blistering as per ASTM D1654, D610 and D714.

      - The finish shall pass an ASTM D870 Water Immersion test of a minimum of 500 hours with no measurable with no rusting or blistering as per ASTM D610 and D714.

      - The finish shall have an impact resistance of 100 inch-pounds in accordance with ASTM D2794.

    - All components shall have a custom finish in a color to match a customer supplied sample.

- Mounting Frame:

  - The diffuser shall be supplied with a frame suitable for (select one):

    - T-bar lay-in mounting with acoustic tile and plenum by others. The tile thickness shall be [1/2 inch], [5/8 inch], or [3/4 inch]. The panel size shall be [24 x 24 inches], [26 x 26 inches], [28 x 28 inches], or [30 x 30 inches].

    - Ceiling or wall surface mounting.

    - Surface mounting with a panel.

- Fastening:

  - The diffuser shall be supplied with (select one):

    - Straight holes.

    - Countersunk holes [with panel mounting frame only].

    - No screw holes [default for T-bar lay in].

2.03	Air Nozzle Diffuser with Core

- Description:

  - Furnish and install Price model ANR nozzle diffusers of sizes and mounting styles shown on the plans and air distribution schedule.

- Construction:

  - The air nozzle diffuser shall be aluminum construction, with a series of concentric round nozzles.

  - The inner nozzle assembly shall be manually adjustable to produce a swivel range of +/- 30 degrees..

- Paint Specification:

  - Paint finish shall have a baked-on powder coat finish.

- Mounting Frame:

  - The diffuser shall be supplied with a frame suitable for ceiling or wall surface mounting.

- Fastening:

  - The diffuser shall be supplied with (select one):

    - EZ fastener [3 inch to 5 inch size only].

    - Concealed mounting ring [6 inch to 16 inch size only].

2.04	Air Nozzle Diffuser without Core

- Description:

  - Furnish and install Price model ANF nozzle diffusers of sizes and mounting styles shown on the plans and air distribution schedule.

- Construction:

  - The air nozzle diffuser shall be aluminum construction.

- Paint Specification:

  - Paint finish shall have a baked-on powder coat finish.

- Mounting Frame:

  - The diffuser shall be supplied with a frame suitable for ceiling or wall surface mounting.

- Fastening:

  - The diffuser shall be supplied with (select one):

    - EZ fastener [3 inch to 5 inch size only].

    - Concealed mounting ring [6 inch to 16 inch size only].

PART 3 – EXECUTION

3.01	Examination

- Verify that conditions are suitable for installation.

- Verify that field measurements are as shown on the drawings.

3.02 	Installation

- Install in accordance with manufacturer’s instructions.

- See drawings for the size(s) and locations of diffusers.

3.03 	Field Quality Control

- See Section 01 40 00 – Quality Requirements for additional requirements.

3.05 	Cleaning

- See Section 01 74 19 – Construction Waste Management and Disposal for additional requirements.

3.06 	Closeout Activities

- See Section 01 78 00 – Closeout Submittals for closeout documentation requirements.

- See Section 01 79 00 – Demonstration and Training for additional requirements.