Price Lattice Face Grille

Division 23 – Heating, Ventilating, and Air Conditioning

Section 23 37 13 – Diffusers, Registers, and Grilles

The following specification is for a defined application. Price would be pleased to assist in developing a specification for your specific need.

PART 1 – GENERAL

  - Section includes:

- Lattice Face Supply Grille.

  - Related Requirements

- Section 01 30 00 – Administrative Requirements

- Section 01 40 00 – Quality Requirements

- Section 01 74 21 – Construction/Demolition Waste Management and Disposal

- Section 01 78 00  – Closeout Submittals

- Section 01 79 00 – Demonstration and Training

  - Reference Standards

- All referenced standards and recommended practices in this section pertain to the most recent publication thereof, including all addenda and errata.

- ASHRAE Standard 55 – Thermal Environmental Conditions for Human Occupancy

- ASHRAE Standard 70 – Method of Testing the Performance of Air Outlets and Air Inlets

ASTM B117 – Standard Practice for Operating Salt Spray (Fog) Apparatus

ASTM D610 – Standard Practice for Evaluating Degree of Rusting on Painted Steel Surfaces

ASTM D714 – Test Method for Evaluating Degree of Blistering of Paints

ASTM D870 – Standard Practice for Testing Water Resistance of Coatings Using Water Immersion

ASTM D1654 – Standard Test Method for Evaluation of Painted or Coated Specimens Subjected to Corrosive Environments

ASTM D2794 – Standard Test Method for Resistance of Organic Coatings to the Effects of Rapid Deformation (Impact)

ASTM D3363 – Standard Test Method for Film Hardness by Pencil Test

NFPA 90A – Standard for the Installation of Air-Conditioning and Ventilating Systems

UL181 – Standard for Factory-Made Air Ducts and Air Connectors

UL/ULC – Underwriters Laboratories Fire Resistance Directory/Underwriters Laboratories of Canada Equipment and Materials Directory

1.04	Submittals

- See Section 01 30 00 – Administrative Requirements for submittal procedures.

- Product Data: Provide data indicating configuration, general assembly, and materials used in fabrication. Include catalog performance ratings that indicate air flow, and NC designation.

- Shop Drawings: Indicate configuration, general assembly, and materials used in fabrication.

- Project Record Documents:  Record actual locations of units and control components.

- Operation and Maintenance Data:  Include manufacturer's descriptive literature, operating instructions (if applicable), and maintenance and repair data.

- Warranty:  Submit manufacturer warranty and ensure forms have been completed in Owner's name and registered with manufacturer.

- Maintenance Materials:  Furnish the following for Owner's use in maintenance of project.

## 1.05	Quality Assurance

- Manufacturer Qualifications:  Company specializing in manufacturing the type of products specified in this section, with minimum ten years of documented experience.

## 1.06	Warranty

- See Section 01 78 00 - Closeout Submittals, for additional warranty requirements.

- Provide 12 month manufacturer warranty from date of shipment of grilles and registers.

PART 2 – PRODUCTS

2.01	Lattice Face Grilles - General

- Basis of Design: Price Industries, Inc.

- Lattice Face Supply Grille: Model LG

- General:

  - The lattice face grille shall be supplied with a lattice [steel], [aluminum], or [stainless steel] face for high capacity applications with low sound and pressure drop.

2.02	Lattice Face Grilles

- Description:

  - Furnish and install Price Model LG lattice face grilles of sizes and mounting types designated by the plans and air distribution schedule.

- Construction:

  - Grilles shall consist of a lattice face with [1/2 inch], [3/4 inch], [1 inch], [2x 1/2 inch] or [1 7/8 x 3/8inch] mesh holes.

  - The lattice face construction shall be (select one):

    - 14-gauge Steel.

    - 14-gauge Aluminum.

    - 20-gauge 304 Stainless steel.

- Paint Specification:

  - Paint finish shall be (select one):

    - Baked-on powder coat finish.

      - The paint film thickness shall be a minimum of 2 mils.

      - The finish shall have a hardness of 2H as tested in accordance with ASTM D3363.

      - The finish shall pass an ASTM B117 Corrosive Environment Salt Spray Test for 1000 hours with no measurable creep, rusting or blistering as per ASTM D1654, D610 and D714.

      - The finish shall pass an ASTM D870 Water Immersion test of a minimum of 500 hours with no measurable with no rusting or blistering as per ASTM D610 and D714.

      - The finish shall have an impact resistance of 100 inch-pounds in accordance with ASTM D2794.

    - Brushed stainless steel finish.

- Options (select all that apply):

  - Fastening:

    - The grille shall be supplied with the following fastening method (select one):

  - Straight holes.

  - No screw holes.

- Dampers:

  - The grille shall incorporate an opposed blade type damper in steel construction.

PART 3 – EXECUTION

3.01	Examination

- Verify that conditions are suitable for installation.

- Verify that field measurements are as shown on the drawings.

3.02 	Installation

- Install in accordance with manufacturer’s instructions.

- See drawings for the size(s) and locations of grilles and registers.

3.03 	Field Quality Control

- See Section 01 40 00 – Quality Requirements for additional requirements.

3.05 	Cleaning

- See Section 01 74 19 – Construction Waste Management and Disposal for additional requirements.

3.06 	Closeout Activities

- See Section 01 78 00 – Closeout Submittals for closeout documentation requirements.

- See Section 01 79 00 – Demonstration and Training for additional requirements.