Price Maximum Security Risk Resistant Perforated Grille

Division 23 – Heating, Ventilating, and Air Conditioning

Section 23 37 13 – Diffusers, Registers, and Grilles

The following specification is for a defined application. Price would be pleased to assist in developing a specification for your specific need.

PART 1 – GENERAL

  - Section includes:

- Maximum Security Risk Resistant Perforated Grille

  - Related Requirements

- Section 01 30 00 – Administrative Requirements

- Section 01 40 00 – Quality Requirements

- Section 01 60 00 – Product Requirements

- Section 01 74 21 – Construction/Demolition Waste Management and Disposal

- Section 01 78 00 – Closeout Submittals

- Section 01 79 00 – Demonstration and Training

  - Reference Standards

- All referenced standards and recommended practices in this section pertain to the most recent publication thereof, including all addenda and errata.

- ASHRAE Standard 70 – Method of Testing the Performance of Air Outlets and Air Inlets

- ASTM 610 – Standard Practice for Evaluating Degree of Rusting on Painted Steel Surfaces

- ASTM 714 – Test Method for Evaluating Degree of Blistering of Paints

- ASTM D1308 – Standard Test Method for Effect of Household Chemicals on Clear and Pigmented Organic Finishes

- ASTM D1654 – Standard Test Method for Evaluation of Painted or Coated Specimens Subjected to Corrosive Environments

- ASTM D4752 – Standard Practice for Measuring MEK Resistance of Ethyl Silicate (Inorganic) Zinc-Rich Primers by Solvent Rub

1.04	Submittals

- See Section 01 30 00 – Administrative Requirements for submittal procedures.

- Product Data: Provide data indicating configuration, general assembly, and materials used in fabrication. Include catalog performance ratings that indicate airflow, static pressure and NC designation.

- Shop Drawings: Indicate configuration, general assembly, and materials used in fabrication.

- Project Record Documents:  Record actual locations of units and control components.

- Operation and Maintenance Data:  Include manufacturer's descriptive literature, operating instructions (if applicable), and maintenance and repair data.

- Warranty:  Submit manufacturer warranty and ensure forms have been completed in Owner's name and registered with manufacturer.

- Maintenance Materials:  Furnish the following for Owner's use in maintenance of project.

## 1.06	Quality Assurance

- Manufacturer Qualifications:  Company specializing in manufacturing the type of products specified in this section, with minimum ten years of documented experience.

## 1.07	Warranty

- See Section 01 7800 - Closeout Submittals, for additional warranty requirements.

- Provide 12 month manufacturer warranty from date of shipment of grilles and registers.

PART 2 – PRODUCTS

2.01	Maximum Security Risk Resistant Perforated Grille

- Basis of Design: Price Industries, Inc.

- Maximum Security Risk Resistant Perforated Grille Model MSRRP

2.02	Maximum Security Risk Resistant Perforated Grille

- Description:

  - Furnish and install Price Model MSRRP Maximum Security Risk Resistant Perforated Grilles of sizes and mounting types designated by the plans and air distribution schedule.

- Construction:

  - The Grille face shall be 3/16” hot rolled steel with 3/16” diameter holes staggered 60 degree on 9/32” centers.

  - The face plate shall be stich welded to 3/16” hot rolled steel sleeve

  - Sleeve shall be (specify length) with stitch welded seams.

- Paint Specification:

  - Paint finish shall be (select one):

    - All components shall have a baked-on powder coat finish.

      - The paint finish must demonstrate no degradation when tested in accordance with ASTM D1308 (covered and spot immersion) and ASTM D4752 (MEK double rub) paint durability tests.

      - The paint film thickness shall be a minimum of 2.0 mils.

      - The finish shall have a hardness of 2H.

      - The finish shall withstand a minimum salt spray exposure of 1000 hours with no measurable creep in accordance with ASTM D1654, and 1000 hours of exposure with no rusting or blistering as per ASTM D610 and ASTM D714.

      - The finish shall have an impact resistance of 80 inch-pounds.

    - All components shall have a custom finish in a color to match a customer supplied sample.

- Options:

.

  - Mounting Frames: (not available with countersunk screw fastening)

    - The grille shall be supplied with (select one):

      - 1”x1”x3/16” hot rolled steel angle frame shipped loose for field welding

      - 11/2”x11/2”x3/16” hot rolled steel angle frame shipped loose for bolting

      - 1”x1”x1/8” hot rolled steel angle frame shipped loose for field welding

      - 11/8”x11/8” hot rolled steel angle frame shipped loose for bolting

  - Fastening:

    - The grille shall be supplied with the following fastening method (select one):

- Countersunk screw holes complete with screws.

- ¾” diameter x 3” masonry rods

- ¾” diameter bent out masonry tabs

  - Sleeve Options

    - Continuously welded seam.

    - Bent out rear flange ( not available with mounting frame)

3. Opposed Blade Damper

a. 	The Grille shall be supplied with a coated steel opposed blade damper. The damper shall be mounted in the wall sleeve and be     operable from the rear of the diffuser.

4. Barrier Bars (not available with countersunk screw fastening)

- The grille shall be supplied with (select one)

1. Hot rolled steel bars (1/2”, ¾”, 1”) diameter

2. Hardened steel bars in sockets (1/2”, ¾”, 1”) diameter

3. 2”x1/4” flat hot rolled steel bars

4. ¾” diameter hot rolled steel vertical bars, 2”x1/4” flat horizontal bars

PART 3 – EXECUTION

3.01	Examination

- Verify that conditions are suitable for installation.

- Verify that field measurements are as shown on the drawings.

3.02 	Installation

- Install in accordance with manufacturer’s instructions.

- See drawings for the size(s) and locations of grilles and registers.

3.03 	Field Quality Control

- See Section 01 40 00 – Quality Requirements for additional requirements.

3.05 	Cleaning

- See Section 01 74 19 – Construction Waste Management and Disposal for additional requirements.

3.06 	Closeout Activities

- See Section 01 78 00 – Closeout Submittals for closeout documentation requirements.

- See Section 01 79 00 – Demonstration and Training for additional requirements.